## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
01.08.16 | 7.2 | 18 | 0 | 1020 | 441 | 273 | 168 | 93 | 6 | 10 | 104 | 870 | 98
02.08.16 | 7.12 | 20 | 0 | 1015 | 433 | 260 | 173 | 101 | 6.1 | 10.1 | 102 | 863 | 96
03.08.16 | 7.6 | 18 | 0 | 890 | 437 | 273 | 164 | 109 | 6.1 | 10.1 | 100 | 860 | 90
04.08.16 | 7.52 | 16 | 0 | 885 | 441 | 265 | 176 | 93 | 6 | 10 | 100 | 854 | 90
05.08.16 | 7.32 | 18 | 0 | 893 | 441 | 273 | 168 | 93 | 6 | 10 | 100 | 893 | 88
06.08.16 | 7.38 | 18 | 0 | 890 | 445 | 227 | 218 | 117 | 6 | 10 | 100 | 853 | 90
07.08.16 | 7.42 | 18 | 0 | 882 | 442 | 225 | 217 | 108 | 6.1 | 10.1 | 100 | 852 | 94
08.08.16 | 7.54 | 20 | 0 | 872 | 441 | 218 | 223 | 101 | 6.1 | 10.12 | 102 | 850 | 92
09.08.16 | 7.33 | 21 | 0 | 875 | 437 | 223 | 214 | 102 | 6.2 | 10.2 | 102 | 853 | 90
10.08.16 | 7.25 | 24 | 0 | 820 | 437 | 218 | 219 | 93 | 6 | 10 | 100 | 848 | 98
11.08.16 | 7.3 | 21 | 0 | 800 | 432 | 239 | 193 | 109 | 6 | 10 | 102 | 854 | 97
12.08.16 | 8.02 | 24 | 0 | 790 | 437 | 218 | 219 | 102 | 6 | 10 | 100 | 851 | 98
13.08.16 | 7.93 | 20 | 0 | 806 | 440 | 228 | 212 | 109 | 6.1 | 10.1 | 102 | 848 | 94
14.08.16 | 7.88 | 18 | 0 | 790 | 432 | 222 | 210 | 106 | 6.2 | 10.2 | 104 | 846 | 95
15.08.16 | 7.82 | 18 | 0 | 788 | 438 | 226 | 212 | 104 | 6 | 10 | 102 | 845 | 94
16.08.16 | 7.7 | 18 | 0 | 810 | 433 | 223 | 210 | 103 | 6.2 | 10.2 | 101 | 851 | 96
17.08.16 | 7.52 | 17 | 0 | 809 | 433 | 231 | 202 | 117 | 6.1 | 10.1 | 100 | 846 | 98
18.08.16 | 7.62 | 18 | 0 | 820 | 440 | 230 | 210 | 108 | 6.1 | 10.1 | 102 | 848 | 98
19.08.16 | 7.7 | 23 | 0 | 722 | 449 | 227 | 212 | 125 | 6.1 | 10.1 | 100 | 834 | 99
20.08.16 | 7.65 | 22 | 0 | 710 | 428 | 218 | 210 | 132 | 6.1 | 10.1 | 105 | 851 | 97
21.08.16 | 7.6 | 21 | 0 | 748 | 430 | 220 | 210 | 109 | 6.1 | 10.1 | 105 | 848 | 98
22.08.16 | 7.54 | 22 | 0 | 750 | 432 | 222 | 210 | 110 | 6.2 | 10.2 | 104 | 854 | 98
23.08.16 | 7.2 | 21 | 0 | 780 | 428 | 214 | 214 | 125 | 6 | 10 | 102 | 842 | 95
24.08.16 | 7.27 | 20 | 0 | 715 | 420 | 210 | 210 | 117 | 6.2 | 10.2 | 101 | 849 | 95
25.08.16 | 7.39 | 22 | 0 | 710 | 412 | 208 | 204 | 115 | 6.1 | 10.1 | 100 | 853 | 98
26.08.16 | 7.42 | 21 | 0 | 687 | 433 | 223 | 210 | 109 | 6.2 | 10.2 | 100 | 845 | 100
27.08.16 | 7.32 | 22 | 0 | 670 | 416 | 203 | 213 | 111 | 6 | 10 | 102 | 845 | 93
28.08.16 | 7.78 | 23 | 0 | 680 | 416 | 203 | 213 | 116 | 6.2 | 10.2 | 100 | 850 | 95
29.08.16 | 7.35 | 23 | 0 | 678 | 410 | 212 | 198 | 116 | 6.2 | 10.2 | 100 | 859 | 97
30.08.16 | 7.53 | 24 | 0 | 672 | 412 | 210 | 212 | 113 | 6.1 | 10.1 | 102 | 868 | 95
31.08.16 | 7.75 | 34 | 0 | 709 | 424 | 269 | 155 | 188 | 6.1 | 10.1 | 100 | 870 | 100
MIN. | 7.12 | 16 | 0 | 670 | 410 | 203 | 155 | 93 | 6 | 10 | 100 | 834 | 88
MAX. | 8.02 | 34 | 0 | 1020 | 449 | 273 | 223 | 188 | 6.2 | 10.2 | 105 | 893 | 100
AVG. | 7.5152 | 20.7419 | 0 | 796.3226 | 431.9355 | 229.3871 | 202.5484 | 111.4194 | 6.0935 | 10.0942 | 101.4194 | 853.3226 | 95.3548
No. of < Spec | 14 | -- | 31 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 1 | 16 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 45.1613 | -- | 100 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 3.2258 | 51.6129 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0