## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
01.09.15 | 7.8 | 16 | 0.1 | 1280 | 516 | 348 | 168 | 135 | 7.2 | 10.2 | 154 | 865 | 112
02.09.15 | 7.54 | 16 | 0.5 | 1285 | 540 | 368 | 172 | 164 | 7.1 | 10.1 | 151 | 856 | 110
03.09.15 | 7.68 | 16 | 0.2 | 1310 | 548 | 392 | 1546 | 157 | 7.1 | 10.1 | 156 | 847 | 115
04.09.15 | 7.62 | 15 | 0.3 | 1295 | 564 | 396 | 168 | 178 | 6.9 | 10.9 | 148 | 840 | 119
05.09.15 | 7.92 | 16 | 0.1 | 1360 | 560 | 404 | 156 | 185 | 6.8 | 11 | 145 | 878 | 116
06.09.15 | 7.83 | 16 | 0.2 | 1300 | 556 | 408 | 148 | 178 | 6.5 | 10.9 | 152 | 865 | 120
07.09.15 | 7.51 | 15 | 0.1 | 1320 | 572 | 376 | 196 | 157 | 6.7 | 10.6 | 154 | 856 | 118
08.09.15 | 7.5 | 17 | 0.2 | 1360 | 564 | 380 | 184 | 164 | 6.8 | 10.38 | 152 | 849 | 116
09.09.15 | 7.5 | 16 | 0.1 | 1340 | 604 | 396 | 208 | 206 | 6.6 | 106 | 148 | 857 | 120
10.09.15 | 7.92 | 15 | 0.2 | 1390 | 596 | 380 | 216 | 221 | 7.2 | 11.2 | 152 | 841 | 115
11.09.15 | 7.75 | 15 | 0.1 | 1360 | 644 | 428 | 216 | 206 | 6.8 | 10.8 | 145 | 848 | 118
12.09.15 | 7.76 | 16 | 0.1 | 1320 | 604 | 404 | 200 | 185 | 7 | 10.6 | 140 | 887 | 115
13.09.15 | 7.51 | 17 | 0.1 | 1250 | 596 | 380 | 216 | 178 | 7.2 | 10.8 | 152 | 830 | 110
14.09.15 | 7.8 | 17 | 0.2 | 1340 | 564 | 372 | 189 | 188 | 7 | 10.8 | 160 | 851 | 115
15.09.15 | 7.54 | 17 | 0.1 | 1450 | 554 | 348 | 206 | 178 | 6.8 | 10.6 | 145 | 862 | 112
16.09.15 | 7.65 | 15 | 0.2 | 1430 | 540 | 344 | 196 | 165 | 6.9 | 10.4 | 148 | 851 | 110
17.09.15 | 7.6 | 16 | 0.1 | 1410 | 524 | 368 | 156 | 175 | 7 | 10.2 | 152 | 862 | 115
18.09.15 | 7.7 | 17 | 0.2 | 1370 | 516 | 344 | 172 | 177 | 7.2 | 10.5 | 148 | 851 | 112
19.09.15 | 7.6 | 17 | 0.1 | 1425 | 524 | 352 | 152 | 185 | 7 | 10.6 | 160 | 865 | 113
20.09.15 | 7.54 | 15 | 0.3 | 1435 | 552 | 392 | 160 | 156 | 6.9 | 10.5 | 162 | 848 | 116
21.09.15 | 7.56 | 15 | 0.2 | 1370 | 524 | 366 | 158 | 142 | 6.8 | 10.8 | 145 | 854 | 115
22.09.15 | 7.56 | 17 | 0.1 | 1450 | 556 | 392 | 164 | 152 | 7 | 10.4 | 152 | 856 | 113
23.09.15 | 7.86 | 18 | 0.1 | 1380 | 584 | 380 | 204 | 194 | 7.2 | 10.6 | 148 | 848 | 112
24.09.15 | 7.7 | 18 | 0.2 | 1420 | 596 | 398 | 198 | 150 | 7 | 10.5 | 145 | 857 | 115
25.09.15 | 7.5 | 17 | 0.2 | 1440 | 588 | 392 | 196 | 168 | 7.2 | 10.3 | 145 | 942 | 119
26.09.15 | 7.55 | 18 | 0.1 | 1450 | 584 | 382 | 202 | 152 | 7.2 | 10.5 | 142 | 930 | 117
27.09.15 | 7.5 | 17 | 0.21 | 1440 | 580 | 378 | 202 | 162 | 7.1 | 10.4 | 145 | 938 | 119
28.09.15 | 7.7 | 17 | 0.1 | 1380 | 592 | 392 | 200 | 172 | 7.2 | 10.5 | 140 | 847 | 117
29.09.15 | 7.7 | 18 | 0.1 | 1370 | 594 | 398 | 196 | 154 | 7 | 10.6 | 142 | 859 | 115
30.09.15 | 7.65 | 17 | 0.1 | 1350 | 610 | 410 | 200 | 134 | 7.2 | 10.2 | 140 | 849 | 117
MIN. | 7.5 | 15 | 0.1 | 1250 | 516 | 344 | 148 | 134 | 6.5 | 10.1 | 140 | 830 | 110
MAX. | 7.92 | 18 | 0.5 | 1450 | 644 | 428 | 1546 | 221 | 7.2 | 106 | 162 | 942 | 120
No. of < Spec | 0 | -- | 16 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 0 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 53.3333 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0