## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.03.23 | 8 | 70 | 0.2 | 2046 | 1371 | 613 | 370 | 243 | 366 | 5.8 | 114 | NIL | 0.3 | 70 | 874 | 114
02.03.23 | 8.2 | 72 | 0.6 | 2104 | 1410 | 622 | 384 | 238 | 370 | 5.9 | 118 | NIL | 0.2 | 72 | 893 | 120
03.03.23 | 8.2 | 72 | 0.7 | 1978 | 1325 | 613 | 378 | 204 | 365 | 5.8 | 116 | NIL | 0.2 | 72 | 754 | 124
04.03.23 | 8.2 | 58 | 0.1 | 1866 | 1250 | 596 | 364 | 232 | 360 | 5.7 | 118 | NIL | 0.2 | 58 | 901 | 120
05.03.23 | 8.2 | 58 | 0.1 | 1866 | 1250 | 596 | 364 | 232 | 360 | 5.7 | 118 | NIL | 0.2 | 58 | 901 | 120
06.03.23 | 8.2 | 55 | 0.1 | 1806 | 1210 | 596 | 340 | 256 | 297 | 5.8 | 120 | NIL | 0.3 | 55 | 890 | 116
07.03.23 | 8.1 | 49 | 0.1 | 1836 | 1230 | 554 | 336 | 218 | 320 | 5.6 | 110 | NIL | 0.2 | 49 | 927 | 120
09.03.23 | 7.4 | 50 | 0.5 | 2055 | 1377 | 601 | 339 | 262 | 328 | 5.6 | 110 | NIL | 0.2 | 50 | 893 | 126
10.03.23 | 8.3 | 49 | 0.7 | 1582 | 1060 | 538 | 323 | 215 | 297 | 6.2 | 124 | NIL | 0.2 | 49 | 754 | 114
11.03.23 | 8.2 | 30 | 0.2 | 1368 | 912 | 534 | 328 | 206 | 290 | 5.9 | 116 | NIL | 0.2 | 30 | 885 | 118
12.03.23 | 8.2 | 30 | 0.2 | 1368 | 912 | 534 | 328 | 206 | 290 | 5.9 | 116 | NIL | 0.2 | 30 | 885 | 118
13.03.23 | 7.9 | 29 | 0.3 | 1354 | 907 | 529 | 319 | 210 | 289 | 5.8 | 114 | NIL | 0.2 | 29 | 890 | 105
14.03.23 | 7.4 | 49 | 0.3 | 2164 | 1450 | 869 | 504 | 365 | 229 | 6 | 110 | NIL | 0.3 | 49 | 899 | 120
15.03.23 | 8.2 | 40 | 0 | 1478 | 990 | 512 | 302 | 210 | 305 | 6.5 | 120 | NIL | 0.2 | 40 | 878 | 100
16.03.23 | 8.1 | 40 | 0 | 1478 | 990 | 504 | 294 | 210 | 312 | 6.2 | 120 | NIL | 0.2 | 40 | 916 | 119
17.03.23 | 7.8 | 32 | 0 | 1492 | 1000 | 496 | 290 | 206 | 305 | 6.5 | 110 | NIL | 0.2 | 32 | 929 | 112
18.03.23 | 7.9 | 24 | 0 | 1448 | 970 | 500 | 298 | 202 | 320 | 6.6 | 110 | NIL | 0.2 | 24 | 870 | 120
19.03.23 | 7.9 | 24 | 0 | 1448 | 970 | 500 | 298 | 202 | 320 | 6.6 | 110 | NIL | 0.2 | 24 | 870 | 120
20.03.23 | 7.3 | 10 | 0 | 1387 | 929 | 504 | 294 | 198 | 297 | 5.9 | 110 | NIL | 0.2 | 10 | 875 | 126
21.03.23 | 7.6 | 30 | 0.8 | 1423 | 964 | 462 | 300 | 162 | 220 | 6.1 | 114 | NIL | 0.2 | 30 | 888 | 117
22.03.23 | 7.7 | 33 | 0.6 | 1478 | 990 | 449 | 281 | 168 | 213 | 6 | 118 | NIL | 0.2 | 33 | 878 | 110
23.03.23 | 7.1 | 32 | 0.1 | 1463 | 980 | 444 | 273 | 171 | 206 | 6.3 | 100 | NIL | 0.2 | 32 | 881 | 100
24.03.23 | 7.2 | 37 | 0.6 | 1334 | 894 | 433 | 265 | 168 | 198 | 5.9 | 100 | NIL | 0.2 | 37 | 882 | 105
25.03.23 | 7.8 | 36 | 0.6 | 1328 | 890 | 441 | 252 | 189 | 190 | 5.5 | 100 | NIL | 0.2 | 36 | 890 | 115
26.03.23 | 7.8 | 36 | 0.6 | 1328 | 890 | 441 | 252 | 189 | 190 | 5.5 | 100 | NIL | 0.2 | 36 | 890 | 115
27.03.23 | 8.3 | 42 | 0.5 | 1493 | 1000 | 458 | 233 | 225 | 229 | 6.3 | 122 |  | 0.2 | 42 | 891 | 120
28.03.23 | 8.2 | 37 | 0.6 | 1406 | 940 | 462 | 286 | 176 | 236 | 6.6 | 124 | NIL | 0.2 | 37 | 895 | 102
29.03.23 | 7.5 | 44 | 0.5 | 1448 | 970 | 571 | 328 | 243 | 259 | 6.7 | 104 | NIL | 0.3 | 44 | 910 | 120
30.03.23 | 7.4 | 42 | 0.3 | 1672 | 1120 | 580 | 340 | 240 | 267 | 6.4 | 114 | NIL | 0.2 | 42 | 873 | 128
31.03.23 | 7.8 | 45 | 0.5 | 1806 | 1210 | 588 | 349 | 239 | 274 | 6.7 | 100 |  | 0.2 | 45 | 875 | 133
MIN. | 7.1 | 17 | 0 | 1328 | 890 | 433 | 233 | 162 | 142 | 5.8 | 100 | 0 | 0.2 | 10 | 754 | 100
MAX. | 8.3 | 28 | 0.8 | 2164 | 1450 | 869 | 504 | 365 | 370 | 10.5 | 124 | 0 | 0.3 | 72 | 929 | 133
AVG. | 7.87 | 19 | 0.32667 | 1610.1 | 1078.7 | 538 | 320.4 | 216.1667 | 278.8387 | 6.0667 | 112.6667 | 0 | 0.21034 | 41.8333 | 881.2333 | 116.5667
No. of < Spec | 6 | -- | 11 | -- | -- | -- | -- | -- | -- | 15 | -- | -- | -- | -- | -- | --
No. of > Spec | 13 | 29 | 9 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 20 | -- | 36.6667 | -- | -- | -- | -- | -- | -- | 50 | [5 empty] | --
% > Specs. | 43.3333 | 96.6667 | 30 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0