## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-10-30 | 8.11 | 20 | NIL | 1701 | 1140 | 655 | 255 | 400 | 302 | 4.5 | - | NIL | 0.5 |  |  | 168
2023-10-31 | 8.26 | 22 | NIL | 1731 | 1160 | 651 | 217 | 434 | 287 | 4.3 | - | NIL | 0.5 |  |  | 162
[8 empty] | 0 |  |  |  | NIL
MIN. | 8.11 | 17 | 0 | 1701 | 1140 | 651 | 217 | 0 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 162
MAX. | 8.26 | 28 | 0 | 1731 | 1160 | 655 | 255 | 434 | 302 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 168
AVG. | 8.185 | 19 |  | 1716 | 1150 | 653 | 236 | 278 | 243.6667 | 4.4 |  | 0 | 0.5 |  |  | 165
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 2 | -- | -- | -- | -- | -- | --
No. of > Spec | 2 | 1 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- |  | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 100 | 50 |  |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0