## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.09.23 | 7.46 | 22 | NIL | 1567 | 1050 | 622 | 349 | 273 | 260 | 6 | - | NIL | 0.5 |  |  | 122
2023-09-02 | 7.63 | 15 | NIL | 1634 | 1095 | 613 | 357 | 256 | 297 | 6.2 | 100 | NIL | 0.5 |  |  | 115
2023-09-04 | 7.53 | 44 | NIL | 2119 | 1420 | 722 | 357 | 365 | 383 | 6.8 | 100 | NIL | 0.7 |  |  | 179
2023-09-05 | 7.78 | 35 | 0.5 | 1611 | 1080 | 636 | 307 | 329 | 311 | 6.3 | - | NIL | 0.5 |  |  | 117
2023-09-06 | 7.11 | 39 | 0.8 | 1418 | 950 | 629 | 314 | 315 | 297 | 6 | - | NIL | 0.5 |  |  | 119
2023-09-07 | 7.48 | 35 | 0.4 | 1428 | 964 | 690 | 328 | 362 | 322 | 5.9 | - | NIL | 0.5 |  |  | 120
2023-09-08 | 7.52 | 37 | 0.5 | 1396 | 935 | 636 | 310 | 326 | 311 | 5.8 | - | NIL | 0.5 |  |  | 116
2023-09-09 | 7.63 | 33 | 0.5 | 1485 | 995 | 617 | 295 | 322 | 289 | 5.4 | - | NIL | 0.5 |  |  | 111
2023-09-11 | 7.69 | 18 | NIL | 1500 | 1005 | 594 | 275 | 319 | 326 | 5.3 | - | NIL | 0.5 |  |  | 129
2023-09-12 | 7.78 | 19 | 0.1 | 1489 | 998 | 605 | 283 | 322 | 297 | 5.5 | - | NIL | 0.5 |  |  | 121
2023-09-13 | 7.65 | 19 | 0.1 | 1464 | 981 | 598 | 279 | 319 | 311 | 5.1 | - | NIL | 0.5 |  |  | 125
2023-09-14 | 7.64 | 17 | 0.1 |  | 914 | 609 | 291 | 318 | 304 | 5.3 | - | NIL | 0.5 |  |  | 120
2023-09-15 | 8.1 | 15 | NIL | 1348 | 903 | 582 | 268 | 314 | 318 | 5.3 | - | NIL | 0.5 |  |  | 126
2023-09-16 | 7.94 | 14 | NIL | 1210 | 811 | 582 | 256 | 326 | 304 | 5.1 | - | NIL | 0.4 |  |  | 113
2023-09-18 | 7.69 | 23 | NIL |  | 975 | 586 | 248 | 338 | 304 | 5.2 | - | NIL | 0.5 |  |  | 129
2023-09-19 | 7.54 | 24 | NIL | 1488 | 992 | 573 | 240 | 333 | 300 | 5.5 | - | NIL | 0.5 |  |  | 126
2023-09-20 | 7.58 | 16 | 0.4 | 1287 | 862 | 590 | 252 | 338 | 297 | 5.4 | - | NIL | 0.4 |  |  | 127
2023-09-21 | 7.75 | 18 | 0.5 | 1330 | 891 | 598 | 248 | 350 | 311 | 5.2 | - | NIL | 0.5 |  |  | 119
2023-09-22 | 7.9 | 24 | NIL | 1330 | 891 | 594 | 241 | 353 | 305 | 5.1 | - | NIL | 0.5 |  |  | 131
2023-09-23 | 7.6 | 17 | NIL | 1419 | 951 | 590 | 252 | 338 | 289 | 5.3 | - | NIL | 0.4 |  |  | 125
2023-09-25 | 7.76 | 15 | NIL | 1410 | 945 | 586 | 237 | 349 | 282 | 4.5 | - | NIL | 0.2 |  |  | 135
2023-09-26 | 7.62 | 18 | NIL | 1440 | 965 | 590 | 244 | 346 | 289 | 5 | - | NIL | 0.3 |  |  | 132
2023-09-27 | 7.37 | 15 | NIL |  | 1032 | 578 | 233 | 345 | 304 | 5.3 | - | NIL | 0.3 |  |  | 139
2023-09-29 | 8.14 | 15 | NIL | 1728 | 1158 | 613 | 229 | 384 | 318 | 4.9 | - | NIL | 0.4 |  |  | 121
2023-09-30 | 7.95 | 19 | 0.9 | 1723 | 1155 | 594 | 225 | 369 | 326 | 5 | - | NIL | 0.3 |  |  | 123
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
MIN. | 7.11 | 17 | 0.1 | 1210 | 811 | 573 | 225 | 0 | 142 | 5.8 | 100 | 0 | 0.2 | 0 | 0 | 111
MAX. | 8.14 | 28 | 0.9 | 2119 | 1420 | 722 | 357 | 384 | 383 | 10.5 | 100 | 0 | 0.7 | 0 | 0 | 179
AVG. | 7.6736 | 19 | 0.43636 | 1492 | 996.72 | 609.08 | 276.72 | 296.75 | 299.8846 | 5.456 | 100 | 0 | 0.45417 |  |  | 125.6
No. of < Spec | 4 | -- | 3 | -- | -- | -- | -- | -- | -- | 20 | -- | -- | -- | -- | -- | --
No. of > Spec | 2 | 10 | 2 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 16 | -- | 27.2727 | -- | -- | -- | -- | -- | -- | 80 | [5 empty] | --
% > Specs. | 8 | 40 | 18.1818 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  |  | 0