## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.07.23 | 7.4 | 14 | 0.3 | 1992 | 1335 | 620 | 364 | 256 | 254 | 7 | 82 | NIL | 0.5 | 14 | 874 | 122
02.07.23 | 7.4 | 14 | 0.3 | 1992 | 1335 | 620 | 364 | 256 | 254 | 7 | 82 | NIL | 0.5 | 14 | 893 | 115
03.07.23 | 7.3 | 12 | 0.2 | 1976 | 1324 | 642 | 377 | 265 | 250 | 6.8 | 90 | NIL | 0.5 | 12 | 754 | 118
04.07.23 | 7.7 | 16 | 0.1 | 2060 | 1380 | 629 | 364 | 265 | 271 | 6.2 | 93 | NIL | 0.5 | 16 | 901 | 125
06.07.23 | 7.6 | 12 | 0.1 | 2058 | 1379 | 655 | 381 | 274 | 286 | 6.9 | 110 | NIL | 0.5 | 12 | 883 | 128
07.06.23 | 7.6 | 12 | 0.1 | 2058 | 1379 | 655 | 381 | 274 | 286 | 6.9 | 110 | NIL | 0.5 | 12 | 890 | 116
09.07.23 | 7.4 | 16 | 0.1 | 2800 | 1680 | 710 | 407 | 303 | 300 | 7.3 | 89 | NIL | 0.6 | 16 | 754 | 108
10.07.23 | 7.4 | 16 | 0.1 | 2800 | 1680 | 710 | 407 | 303 | 300 | 7.3 | 89 | NIL | 0.6 | 16 | 878 | 149
11.07.23 | 7.8 | 7 | 0 | 2246 | 1504 | 693 | 360 | 333 | 321 | 6.2 | 94 | NIL | 0.7 | 22 | 881 | 136
12.07.23 | 7.5 | 9 | 0 | 2313 | 1550 | 706 | 381 | 325 | 300 | 5.9 | 94 | NIL | 0.6 | 9 | 890 | 135
13.07.23 | 7.5 | 10 | 0 | 2194 | 1470 | 712 | 390 | 322 | 305 | 7 | 100 | NIL | 0.6 | 10 | 894 | 130
14.07.23 | 7.4 | 20 | 0.3 | 1851 | 1240 | 698 | 377 | 321 | 307 | 7.1 | 90 | NIL | 0.5 | 20 | 899 | 129
15.07.23 | 7.4 | 17 | 0.2 | 1701 | 1140 | 668 | 338 | 330 | 286 | 6.9 | 87 | NIL | 0.5 | 17 | 878 | 125
16.07.23 | 7.4 | 17 | 0.2 | 1701 | 1140 | 668 | 338 | 330 | 286 | 6.9 | 87 | NIL | 0.5 | 17 | 916 | 131
17.07.23 | 7.6 | 15 | 0 | 1648 | 1104 | 689 | 351 | 338 | 300 | 7.2 | 92 | NIL | 0.5 | 15 | 929 | 123
18.07.23 | 7.5 | 17 | 0.4 | 2075 | 1390 | 698 | 338 | 360 | 298 | 6.9 | 90 | NIL | 0.5 | 17 | 837 | 132
19.07.23 | 7.3 | 15 | 0.5 | 1716 | 1150 | 651 | 325 | 326 | 286 | 6.5 | 87 | NIL | 0.5 | 15 | 879 | 128
20.07.23 | 7.3 | 17 | 0.4 | 1552 | 1040 | 706 | 347 | 359 | 307 | 7.1 | 84 | NIL | 0.5 | 17 | 875 | 141
21.07.23 | 7.4 | 16 | 0.4 | 1313 | 880 | 629 | 338 | 291 | 286 | 6.5 | 80 | NIL | 0.5 | 16 | 888 | 122
23.07.23 | 7.4 | 32 | 0.1 | 1492 | 1000 | 619 | 344 | 275 | 221 | 6.3 | 90 | NIL | 0.4 | 32 | 881 | 126
24.07.23 | 7.7 | 16 | 0 | 1343 | 900 | 655 | 351 | 304 | 307 | 7.1 | 92 | NIL | 0.5 | 16 | 882 | 139
25.07.23 | 7.6 | 17 | 0 | 1328 | 890 | 638 | 342 | 296 | 286 | 6.9 | 87 | NIL | 0.5 | 17 | 892 | 142
26.07.23 | 7.3 | 18 | 0.4 | 1328 | 890 | 646 | 388 | 258 | 321 | 7.2 | 84 | NIL | 0.5 | 18 | 890 | 133
27.07.23 | 7.6 | 17 | 0.5 | 1463 | 980 | 633 | 325 | 308 | 293 | 6.5 | 89 | NIL | 0.4 | 17 | 887 | 126
28.07.23 | 7.8 | 20 | 0.1 | 1448 | 970 | 620 | 324 | 296 | 260 | 5.9 | 93 | NIL | 0.4 | 20 | 891 | 120
29.07.23 | 7.7 | 21 | 0.1 | 1418 | 950 | 616 | 317 | 299 | 264 | 6 | 90 | NIL | 0.5 | 21 | 910 | 116
30.07.23 | 7.7 | 21 | 0.1 | 1418 | 950 | 616 | 317 | 299 | 264 | 6 | 90 | NIL | 0.5 | 21 | 902 | 116
31.07.23 | 7.6 | 20 | 0.1 | 1403 | 940 | 595 | 324 | 271 | 293 | 6.6 | 89 | NIL | 0.4 | 20 | 873 | 132
MIN. | 7.3 | 17 | 0 | 1313 | 880 | 595 | 317 | 256 | 142 | 5.8 | 80 | 0 | 0.4 | 9 | 754 | 108
MAX. | 7.8 | 28 | 0.5 | 2800 | 1680 | 712 | 407 | 360 | 321 | 10.5 | 110 | 0 | 0.7 | 32 | 929 | 149
AVG. | 7.5107 | 19 | 0.18214 | 1810.25 | 1198.9286 | 657.0357 | 355.7143 | 301.3214 | 280.4828 | 6.7179 | 90.5 | 0 | 0.50741 | 16.75 | 878.6071 | 127.25
No. of < Spec | 13 | -- | 16 | -- | -- | -- | -- | -- | -- | 2 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 3 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 46.4286 | -- | 57.1429 | -- | -- | -- | -- | -- | -- | 7.1429 | [5 empty] | --
% > Specs. | 0 | 10.7143 | 0 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0