## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.06.23 | 8.3 | 20 | 0.1 | 1239 | 830 | 462 | 286 | 176 | 202 | 6 | 122 | NIL | 0.4 | 20 | 874 | 110
02.06.23 | 8.3 | 21 | 0 | 1269 | 850 | 475 | 294 | 181 | 216 | 6.8 | 120 | NIL | 0.4 | 21 | 893 | 115
03.06.23 | 8.2 | 20 | 0 | 1296 | 864 | 484 | 299 | 220 | 220 | 7 | 122 | NIL | 0.4 | 20 | 754 | 119
04.06.23 | 8.2 | 18 | 0 | 1296 | 864 | 484 | 299 | 220 | 220 | 7 | 122 | NIL | 0.4 | 18 | 901 | 120
05.06.23 | 8.1 | 15 | 0.1 | 1253 | 840 | 496 | 298 | 198 | 220 | 6.3 | 119 | NIL | 0.3 | 15 | 898 | 110
06.06.23 | 8 | 12 | 0 | 1462 | 980 | 663 | 375 | 288 | 209 | 6 | 114 | NIL | 0.4 | 12 | 883 | 129
07.06.23 | 7.9 | 16 | 0.1 | 1243 | 833 | 504 | 307 | 197 | 223 | 6.7 | 116 | NIL | 0.3 | 16 | 890 | 116
08.06.23 | 8.2 | 32 | 0 | 1230 | 824 | 496 | 294 | 202 | 221 | 6.4 | 122 | NIL | 0.3 | 32 | 893 | 110
09.06.23 | 8.1 | 30 | 0 | 1319 | 884 | 503 | 298 | 205 | 218 | 6.2 | 120 | NIL | 0.3 | 30 | 754 | 108
10.06.23 | 8.1 | 28 | 0 | 1298 | 870 | 500 | 292 | 208 | 212 | 6 | 118 | NIL | 0.3 | 28 | 885 | 102
11.06.23 | 8.1 | 22 | 0.1 | 1298 | 870 | 574 | 400 | 174 | 244 | 6 | 113 | NIL | 0.4 | 22 | 881 | 120
12.06.23 | 8.1 | 20 | 0 | 1358 | 910 | 506 | 301 | 205 | 250 | 6.5 | 120 | NIL | 0.3 | 20 | 890 | 112
13.06.23 | 7.8 | 27 | 0 | 1492 | 1000 | 514 | 305 | 209 | 257 | 6.8 | 109 | NIL | 0.3 | 27 | 894 | 120
14.06.23 | 7.6 | 37 | 0.2 | 1535 | 1029 | 523 | 318 | 205 | 243 | 7 | 100 | NIL | 0.3 | 37 | 899 | 129
15.06.23 | 7.3 | 35 | 0.2 | 1549 | 1020 | 633 | 342 | 291 | 203 | 6.2 | 98 | NIL | 0.3 | 35 | 878 | 124
16.06.23 | 7.2 | 37 | 0.2 | 1541 | 1033 | 654 | 366 | 288 | 200 | 6.3 | 96 | NIL | 0.3 | 37 | 916 | 131
17.06.23 | 7.9 | 34 | 0.2 | 1572 | 1042 | 670 | 384 | 286 | 214 | 6.9 | 100 | NIL | 0.5 | 34 | 929 | 133
18.06.23 | 7.9 | 34 | 0.2 | 1572 | 1042 | 670 | 384 | 286 | 214 | 6.9 | 100 | NIL | 0.5 | 34 | 837 | 118
19.06.23 | 7.2 | 37 | 0 | 1628 | 1090 | 632 | 362 | 270 | 229 | 6.1 | 104 | NIL | 0.3 | 37 | 879 | 122
20.06.23 | 7.5 | 47 | 0.2 | 1515 | 1015 | 562 | 340 | 198 | 214 | 6.9 | 100 | NIL | 0.3 | 47 | 875 | 116
21.06.23 | 7.6 | 48 | 0.8 | 1582 | 1060 | 589 | 353 | 236 | 207 | 6.5 | 92 | NIL | 0.4 | 48 | 888 | 123
22.06.23 | 7.4 | 32 | 0.1 | 1492 | 1000 | 619 | 344 | 275 | 221 | 6.3 | 90 | NIL | 0.4 | 32 | 878 | 119
23.06.23 | 7.8 | 40 | 0.1 | 1557 | 1043 | 628 | 349 | 279 | 214 | 7.1 | 87 | NIL | 0.4 | 40 | 881 | 126
24.06.23 | 7.9 | 16 | 0.4 | 1672 | 1128 | 612 | 383 | 229 | 262 | 7 | 96 | NIL | 0.5 | 16 | 882 | 126
25.06.23 | 7.9 | 16 | 0.4 | 1672 | 1128 | 612 | 383 | 229 | 262 | 7 | 96 | NIL | 0.5 | 16 | 892 | 114
26.06.23 | 7.4 | 12 | 0.2 | 1688 | 1131 | 608 | 360 | 248 | 279 | 6.8 | 93 | NIL | 0.5 | 12 | 890 | 130
27.06.23 | 7.5 | 13 | 0.2 | 1642 | 1100 | 616 | 355 | 261 | 250 | 6.9 | 84 | NIL | 0.5 | 13 | 887 | 123
28.06.23 | 7.6 | 14 | 0.6 | 1815 | 1240 | 625 | 368 | 257 | 257 | 6.6 | 92 | NIL | 0.6 | 14 | 891 | 136
29.06.23 | 7.4 | 13 | 0.5 | 1791 | 1200 | 612 | 342 | 270 | 264 | 6.5 | 80 | NIL | 0.5 | 13 | 910 | 145
30.06.23 | 7.8 | 14 | 0.5 | 1780 | 1193 | 600 | 332 | 268 | 260 | 6.7 | 87 | NIL | 0.5 | 14 | 873 | 140
MIN. | 7.2 | 17 | 0 | 1230 | 824 | 462 | 286 | 174 | 142 | 5.8 | 80 | 0 | 0.3 | 12 | 754 | 102
MAX. | 8.3 | 28 | 0.8 | 1815 | 1240 | 670 | 400 | 291 | 279 | 10.5 | 122 | 0 | 0.6 | 48 | 929 | 145
AVG. | 7.81 | 19 | 0.18 | 1488.5333 | 997.1 | 570.8667 | 337.1 | 235.3 | 227.3226 | 6.58 | 104.4 | 0 | 0.3931 | 25.3333 | 879.1667 | 121.5333
No. of < Spec | 6 | -- | 16 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 10 | 16 | 2 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 20 | -- | 53.3333 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 33.3333 | 53.3333 | 6.6667 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0