## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.04.22 | 8.5 | 18 | 0 | 2228 | 1493 | 706 | 412 | 294 | 247 | 5 | 133 | NIL | 0.2 | 18 | 874 | 155
02.04.22 | 8.1 | 18 | 0 | 2149 | 1440 | 714 | 424 | 290 | 261 | 5.6 | 122 | NIL | 0.2 | 18 | 754 | 149
03.04.22 | 8.1 | 18 | 0 | 2149 | 1440 | 714 | 424 | 290 | 261 | 5.6 | 122 | NIL | 0.2 | 18 | 754 | 149
04.04.22 | 8 | 20 | 0.2 | 1985 | 1350 | 702 | 389 | 313 | 254 | 5.2 | 122 | NIL | 0.2 | 20 | 893 | 140
05.04.22 | 8.4 | 20 | 0.2 | 2045 | 1370 | 714 | 413 | 301 | 212 | 5.9 | 130 | NIL | 0.2 | 20 | 878 | 145
06.04.22 | 8.1 | 26 | 0.2 | 2048 | 1370 | 706 | 390 | 316 | 265 | 5.5 | 125 | NIL | 0.2 | 26 | 873 | 144
07.04.22 | 8.2 | 30 | 0.2 | 2179 | 1460 | 692 | 378 | 314 | 275 | 5.8 | 126 | NIL | 0.2 | 30 | 893 | 142
08.04.22 | 8.232 | 32 | 0.2 | 2006 | 1344 | 685 | 374 | 311 | 283 | 6.2 | 133 | NIL | 0.2 | 32 | 754 | 140
09.04.22 | 8.1 | 25 | 0.2 | 1850 | 1240 | 731 | 357 | 374 | 294 | 6.5 | 122 | NIL | 0.2 | 25 | 894 | 145
10.04.22 | 8.1 | 25 | 0.2 | 1850 | 1240 | 731 | 357 | 374 | 294 | 6.5 | 122 | NIL | 0.2 | 25 | 894 | 145
11.04.22 | 8.5 | 18 | 0.1 | 1701 | 1140 | 672 | 349 | 323 | 287 | 6 | 129 | NIL | 0.2 | 18 | 890 | 139
12.04.22 | 8.4 | 19 | 0.1 | 1737 | 1164 | 680 | 361 | 319 | 298 | 6.3 | 133 | NIL | 0.2 | 19 | 899 | 147
13.04.22 | 8.4 | 24 | 0.2 | 1733 | 1120 | 672 | 357 | 315 | 305 | 6.4 | 133 | NIL | 0.2 | 24 | 878 | 150
14.04.22 | 7.3 | 16 | 0 | 1836 | 1230 | 693 | 374 | 319 | 308 | 6.7 | 119 | NIL | 0.2 | 16 | 916 | 152
15.04.22 | 8 | 20 | 0 | 1770 | 1210 | 692 | 369 | 323 | 302 | 6.2 | 128 | NIL | 0.2 | 20 | 929 | 144
16.04.22 | 8.1 | 18 | 0 | 1704 | 1142 | 672 | 353 | 319 | 290 | 6 | 122 | NIL | 0.2 | 18 | 929 | 140
17.04.22 | 8.1 | 18 | 0 | 1704 | 1142 | 672 | 353 | 319 | 290 | 6 | 122 | NIL | 0.2 | 18 | 929 | 140
18.04.22 | 8.3 | 22 | 0 | 2222 | 1489 | 605 | 357 | 248 | 279 | 5.9 | 130 | NIL | 0.2 | 22 | 875 | 139
19.04.22 | 8.2 | 20 | 0 | 1803 | 1202 | 613 | 314 | 299 | 290 | 6.9 | 128 | NIL | 0.2 | 20 | 888 | 136
20.04.22 | 8.1 | 24 | 0 | 1646 | 1103 | 588 | 353 | 235 | 298 | 6 | 122 | NIL | 0.2 | 24 | 878 | 130
21.04.22 | 7.6 | 28 | 0 | 1734 | 1162 | 609 | 374 | 235 | 301 | 6.2 | 120 | NIL | 0.2 | 28 | 881 | 139
22.04.22 | 7.7 | 19 | 0 | 1615 | 1082 | 622 | 386 | 236 | 290 | 5.9 | 122 | NIL | 0.2 | 19 | 884 | 142
23.04.22 | 8.3 | 30 | 0 | 1701 | 1140 | 638 | 412 | 226 | 308 | 5.5 | 128 | NIL | 0.2 | 30 | 884 | 149
24.04.22 | 8.3 | 30 | 0 | 1701 | 1140 | 638 | 412 | 226 | 308 | 5.5 | 128 | NIL | 0.2 | 30 | 884 | 149
25.04.22 | 8.5 | 23 | 0 | 1866 | 1250 | 664 | 428 | 236 | 316 | 5.8 | 135 | NIL | 0.2 | 23 | 890 | 153
26.04.22 | 8.6 | 25 | 0 | 1955 | 1310 | 672 | 441 | 231 | 323 | 6 | 139 | NIL | 0.2 | 25 | 886 | 159
27.04.22 | 8.4 | 22 | 0 | 2212 | 1482 | 685 | 454 | 231 | 327 | 6.7 | 134 | NIL | 0.2 | 22 | 899 | 162
28.04.22 | 8.7 | 23 | 0 | 1806 | 1210 | 706 | 458 | 248 | 316 | 6.5 | 139 | NIL | 0.2 | 23 | 905 | 155
29.04.22 | 8.5 | 18 | 0 | 1915 | 1283 | 714 | 483 | 231 | 305 | 6.2 | 139 | NIL | 0.2 | 18 | 881 | 148
30.04.22 | 8.3 | 20 | 0.1 | 2119 | 1420 | 638 | 462 | 176 | 290 | 5.5 | 129 | NIL | 0.2 | 20 | 890 | 140
MIN. | 7.3 | 17 | 0 | 1615 | 1082 | 588 | 314 | 176 | 142 | 5.8 | 119 | 0 | 0.2 | 16 | 754 | 130
MAX. | 8.7 | 28 | 0.2 | 2228 | 1493 | 731 | 483 | 374 | 327 | 10.5 | 139 | 0 | 0.2 | 32 | 929 | 162
AVG. | 8.2044 | 19 | 0.063333 | 1898.9667 | 1272.2667 | 674.6667 | 392.2667 | 282.4 | 284.4839 | 6 | 127.8667 | 0 | 0.2 | 22.3 | 878.5333 | 145.5667
No. of < Spec | 1 | -- | 22 | -- | -- | -- | -- | -- | -- | 13 | -- | -- | -- | -- | -- | --
No. of > Spec | 25 | 15 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 3.3333 | -- | 73.3333 | -- | -- | -- | -- | -- | -- | 43.3333 | [5 empty] | --
% > Specs. | 83.3333 | 50 | 0 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0