## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.08.23 | 7.4 | 59 | 0.1 | 1676 | 1123 | 650 | 315 | 335 | 264 | 6 | 100 | NIL | 0.5 | 59 | 910 | 135
02.05.23 | 7.9 | 13 | 0.1 | 2537 | 1700 | 907 | 519 | 388 | 328 | 6.3 | 119 | NIL | 0.5 | 13 | 864 | 149
03.05.23 | 7.9 | 15 | 0.1 | 2310 | 1548 | 894 | 506 | 388 | 312 | 6.7 | 116 | NIL | 0.5 | 15 | 754 | 152
04.08.23 | 7.5 | 40 | 0.1 | 2075 | 1390 | 643 | 325 | 318 | 282 | 6.5 | 104 | NIL | 0.6 | 40 | 864 | 142
05.08.23 | 7.4 | 38 | 0 | 2119 | 1420 | 691 | 360 | 331 | 272 | 6.8 | 110 | NIL | 0.6 | 38 | 860 | 136
| 7.8 | 13 | 0 | 2364 | 1584 | 885 | 510 | 375 | 236 | 6 | 114 | NIL | 0.5 | 13 | 873 | 139
07.08.23 | 7.8 | 25 | 0 | 2268 | 1520 | 703 | 366 | 337 | 286 | 6.2 | 113 | NIL | 0.6 | 25 | 910 | 152
08.08.23 | 7.8 | 22 | 0.1 | 2313 | 1550 | 698 | 360 | 338 | 275 | 6 | 102 | NIL | 0.6 | 22 | 910 | 148
09.08.23 | 7.9 | 26 | 0 | 2372 | 1589 | 815 | 437 | 378 | 398 | 6.7 | 110 | NIL | 0.6 | 26 | 864 | 154
10.08.23 | 7.2 | 25 | 0 | 2373 | 1590 | 824 | 445 | 379 | 433 | 7 | 112 | NIL | 0.6 | 25 | 887 | 158
11.08.23 | 7.6 | 28 | 0 | 2376 | 1592 | 818 | 440 | 378 | 438 | 6.9 | 118 | NIL | 0.6 | 28 | 875 | 150
12.08.23 | 7.6 | 24 | 0 | 2448 | 1640 | 820 | 399 | 421 | 391 | 6.5 | 100 | NIL | 0.6 | 24 | 888 | 140
| 7.8 | 68 | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 877 | 152
14.08.23 | 7.514 | 14 | 0 | 2507 | 1680 | 832 | 480 | 352 | 400 | 6.2 | 104 | NIL | 0.6 | 14 | 872 | 144
15.08.23 | 7.4 | 15 | 0 | 2573 | 1700 | 793 | 472 | 321 | 410 | 6.4 | 116 | NIL | 0.6 | 15 | 869 | 150
16.08.23 | 6.9 | 23 | 0.3 | 2229 | 1494 | 800 | 484 | 316 | 424 | 6.9 | 113 | NIL | 0.6 | 23 | 958 | 155
17.08.23 | 7.1 | 36 | 0.1 | 2149 | 1440 | 843 | 496 | 347 | 440 | 7 | 104 | NIL | 0.6 | 36 | 878 | 157
18.08.23 | 7.8 | 31 | 0.6 | 2209 | 1430 | 835 | 389 | 446 | 398 | 6.9 | 114 | NIL | 0.6 | 31 | 871 | 141
19.08.23 | 7.4 | 40 | 0 | 2074 | 1390 | 822 | 411 | 411 | 384 | 7 | 98 | NIL | 0.6 | 40 | 873 | 138
20.05.23 | 7.9 | 34 | 0.4 | 2522 | 1690 | 876 | 510 | 366 | 230 | 6.2 | 114 | NIL | 0.6 | 34 | 864 | 142
21.08.23 | 8.2 | 20 | 0.1 | 2223 | 1489 | 829 | 418 | 411 | 387 | 6.4 | 99 | NIL | 0.6 | 20 | 878 | 134
22.05.23 | 7.4 | 47 | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 881 | 139
23.05.23 | 8 | 55 | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.05.23 | 7.8 | 40 | 0 | 2179 | 1460 | 885 | 510 | 375 | 226 | 6.9 | 114 | NIL | 0.5 | 40 | 982 | 140
25.08.23 | 7.2 | 25 | 0.2 | 2209 | 1480 | 818 | 450 | 368 | 412 | 6.9 | 110 | NIL | 0.6 | 25 | 875 | 138
26.05.23 | 7.5 | 26 | 0 | 2254 | 1510 | 907 | 514 | 393 | 237 | 6.8 | 110 | NIL | 0.5 | 26 | 960 | 147
27.05.23 | 8 | 26 | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 893 | 156
28.05.23 | 8 | 26 | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 888 | 156
29.08.23 | 7.6 | 15 | 0.1 | 2119 | 1420 | 794 | 433 | 361 | 405 | 5.9 | 100 | NIL | 0.5 | 15 | 872 | 139
30.05.23 | 7.7 | 30 | 0.6 | 2090 | 1400 | 881 | 492 | 389 | 223 | 6.4 | 100 | NIL | 0.5 | 30 | 893 | 137
31.05.23 | 7.6 | 33 | 0.5 | 2074 | 1390 | 873 | 480 | 393 | 220 | 6.2 | 112 | NIL | 0.5 | 33 | 890 | 132
MIN | 6.9 | 17 | 0 | 1676 | 1123 | 643 | 315 | 316 | 142 | 5.8 | 98 | 0 | 0.4 | 13 | 754 | 132
MAX. | 8.2 | 28 | 0.9 | 2573 | 1700 | 911 | 532 | 446 | 440 | 10.5 | 120 | 0 | 0.6 | 68 | 984 | 158
AVG. | 7.6327 | 19 | 0.16129 | 2266.129 | 1516.0968 | 825.5484 | 454.1935 | 371.3548 | 319.0938 | 6.5677 | 109.0323 | 0 | 0.55333 | 30.0645 | 887.6452 | 145.0645
No. of < Spec | 9 | -- | 21 | -- | -- | -- | -- | -- | -- | 1 | -- | -- | -- | -- | -- | --
No. of > Spec | 1 | 24 | 3 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 29.0323 | -- | 67.7419 | -- | -- | -- | -- | -- | -- | 3.2258 | [5 empty] | --
% > Specs. | 3.2258 | 77.4194 | 9.6774 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0