## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-12-01 | 7.38 | 79 | NIL | 1934 | 1296 | 1082 | 629 | 453 | 217 | 3.8 | - | NIL | 0.5 |  |  | 138
2023-12-02 | 7.42 | 50 | NIL | 2054 | 1376 | 1008 | 576 | 432 | 246 | 4.2 | - | NIL | 0.5 |  |  | 143
2023-12-04 | 8.19 | 29 | NIL | 2239 | 1500 | 999 | 550 | 449 | 224 | 4.1 | - | NIL | 0.5 |  |  | 160
2023-12-06 | 7.12 | 54 | 0.9 | 1982 | 1328 | 1047 | 590 | 457 | 231 | 4 | - | NIL | 0.5 |  |  | 133
2023-12-14 | 7.21 | 32 | 0.6 | 1820 | 1220 | 950 | 537 | 413 | 244 | 4.4 | - | NIL | 0.5 |  |  | 151
2023-12-15 | 7.09 | 40 | 0.5 | 1715 | 1176 | 937 | 546 | 391 | 252 | 4.2 | - | NIL | 0.5 |  |  | 148
2023-12-16 | 7.46 | 45 | 0.5 | 1910 | 1280 | 928 | 537 | 391 | 244 | 4.3 | - | NIL | 0.5 |  |  | 150
2023-12-18 | 7.1 | 46 | 0.3 | 1611 | 1080 | 937 | 48 | 889 | 289 | 4 | - | NIL | 0.5 |  |  | 139
2023-12-19 | 7.56 | 49 | NIL | 1432 | 960 | 929 | 575 | 354 | 259 | 3.7 | - | NIL | 0.5 |  |  | 88
2023-12-19 | 7.4 | 50 | 0.8 | 1507 | 1010 | 1035 | 731 | 304 | 289 | 3.8 | - | NIL | 0.5 |  |  | 142
2023-12-20 | 7.2 | 70 | 0.9 | 1478 | 990 | 966 | 653 | 313 | 252 | 4.1 | - | NIL | 0.5 |  |  | 138
2023-12-21 | 6.88 | 61 | 0.8 | 1407 | 943 | 975 | 644 | 331 | 259 | 4 | - | NIL | 0.5 |  |  | 140
2023-12-22 | 7.39 | 65 | 0.8 | 1658 | 1111 | 1017 | 658 | 359 | 274 | 3.8 | - | NIL | 0.5 |  |  | 132
2023-12-23 | 7.89 | 61 | NIL | 1697 | 1018 | 1040 | 630 | 410 | 311 | 4.6 | - | NIL | 0.5 |  |  | 138
2023-12-25 | 8.64 | 98 | NIL | 1422 | 953 | 865 | 524 | 341 | 289 | 4.2 | - | NIL | 0.5 |  |  | 135
2023-12-26 | 7.9 | 78 | NIL | 1413 | 947 | 851 | 501 | 350 | 311 | 4.3 | - | NIL | 0.5 |  |  | 141
2023-12-27 | 7.54 | 62 | NIL | 1623 | 1088 | 925 | 469 | 456 | 274 | 2 | - | NIL | 0.5 |  |  | 138
2023-12-28 | 7.56 | 48 | NIL | 1618 | 1083 | 911 | 483 | 428 | 296 | 1.6 | - | NIL | 0.5 |  |  | 135
2023-12-29 | 7.41 | 42 | 1 | 1440 | 965 | 1012 | 621 | 391 | 311 | 1.5 |  | NIL | 0.5 |  |  | 142
2023-12-30 | 7.9 | 35 | NIL | 1461 | 979 | 994 | 543 | 451 | 326 | 1.7 |  | NIL | 0.5 |  |  | 121
NIL
NIL
NIL
NIL
NIL
NIL
NIL
NIL
MIN | 6.88 | 17 | 0.3 | 1407 | 943 | 851 | 48 | 304 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 88
MAX. | 8.64 | 28 | 1 | 2239 | 1500 | 1082 | 731 | 889 | 326 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 160
AVG. | 7.512 | 19 | 0.71 | 1671.05 | 1115.15 | 970.4 | 552.25 | 418.15 | 263.8095 | 3.615 |  | 0 | 0.5 |  |  | 137.6
No. of < Spec | 12 | -- | 0 | -- | -- | -- | -- | -- | -- | 20 | -- | -- | -- | -- | -- | --
No. of > Spec | 2 | 20 | 7 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 60 | -- | 0 | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 10 | 100 | 70 |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0