## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-10-30 | 7.58 | 44 | NIL | 2340 | 1568 | 859 | 325 | 534 | 302 | 3.5 | - | NIL | 0.5 |  |  | 164
2023-10-31 | 7.52 | 35 | NIL | 2268 | 1520 | 841 | 312 | 529 | 280 | 3.7 | - | NIL | 0.5 |  |  | 158
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[11 empty] | - | NIL | 0.5
[12 empty] | NIL | 0.5
[12 empty] | NIL | 0.5
NIL
NIL
NIL
NIL
NIL
NIL
NIL
NIL
MIN | 7.52 | 17 | 0 | 2268 | 1520 | 841 | 312 | 529 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 158
MAX. | 7.58 | 28 | 0 | 2340 | 1568 | 859 | 325 | 534 | 302 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 164
AVG. | 7.55 | 19 |  | 2304 | 1544 | 850 | 318.5 | 531.5 | 241.3333 | 3.6 |  | 0 | 0.5 |  |  | 161
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 2 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 2 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- |  | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 0 | 100 |  |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0