## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.07.23 | 7.6 | 17 | 0.1 | 1940 | 1300 | 600 | 340 | 260 | 240 | 6.2 | 91 | NIL | 0.5 | 17 | 910 | 134
02.07.23 | 7.6 | 17 | 0 | 1940 | 1300 | 600 | 340 | 260 | 240 | 6.2 | 91 | NIL | 0.5 | 17 | 864 | 139
03.07.23 | 7.8 | 19 | 0 | 1865 | 1250 | 612 | 351 | 261 | 243 | 6.5 | 96 | NIL | 0.8 | 19 | 754 | 140
04.07.23 | 7.4 | 20 | 0.3 | 2213 | 1453 | 642 | 368 | 274 | 257 | 6.8 | 100 | NIL | 0.8 | 20 | 864 | 159
06.07.23 | 7.5 | 28 | 0 | 2000 | 1340 | 625 | 342 | 283 | 271 | 7 | 102 | NIL | 0.7 | 28 | 873 | 152
07.07.23 | 7 | 70 | 0 | 2373 | 1590 | 642 | 355 | 287 | 279 | 6.5 | 87 | NIL | 0.7 | 70 | 910 | 157
09.07.23 | 7.9 | 27 | 0 | 1704 | 1142 | 549 | 344 | 205 | 200 | 6.5 | 120 | NIL | 0.4 | 27 | 864 | 130
10.07.23 | 7.5 | 26 | 0 | 2313 | 1550 | 702 | 377 | 325 | 216 | 7.5 | 90 | NIL | 0.7 | 26 | 887 | 169
11.07.23 | 7.3 | 20 | 0 | 2246 | 1504 | 693 | 364 | 329 | 321 | 6.2 | 94 | NIL | 0.7 | 20 | 875 | 136
12.07.23 | 7.6 | 30 | 0.5 | 1963 | 1315 | 689 | 372 | 317 | 293 | 7.2 | 97 | NIL | 0.7 | 30 | 888 | 162
13.07.23 | 7.9 | 28 | 0 | 1970 | 1320 | 678 | 364 | 314 | 290 | 6.9 | 98 | NIL | 0.7 | 28 | 877 | 153
14.07.23 | 7.6 | 24 | 0 | 2239 | 1500 | 693 | 364 | 329 | 286 | 6.7 | 100 | NIL | 0.7 | 24 | 872 | 159
15.07.23 | 7.6 | 24 | 0 | 2015 | 1350 | 685 | 360 | 325 | 270 | 7 | 98 | NIL | 0.7 | 24 | 869 | 152
16.07.23 | 7.6 | 24 | 0 | 2015 | 1350 | 685 | 360 | 325 | 270 | 7 | 98 | NIL | 0.7 | 24 | 958 | 158
17.07.23 | 7.7 | 20 | 0 | 1970 | 1320 | 690 | 355 | 335 | 250 | 6.8 | 100 | NIL | 0.7 | 20 | 878 | 167
18.07.23 | 7.8 | 30 | 0.3 | 2134 | 1430 | 706 | 351 | 355 | 264 | 6.9 | 98 | NIL | 0.7 | 30 | 871 | 158
19.07.23 | 7.3 | 37 | 0.3 | 2090 | 1400 | 687 | 342 | 345 | 243 | 7 | 90 | NIL | 0.7 | 37 | 873 | 153
20.07.23 | 7.7 | 40 | 0.3 | 1940 | 1300 | 710 | 364 | 346 | 279 | 6.9 | 100 | NIL | 0.7 | 40 | 864 | 161
21.07.23 | 7.6 | 39 | 0 | 1910 | 1280 | 676 | 351 | 325 | 271 | 6 | 96 | NIL | 0.7 | 39 | 878 | 150
23.07.23 | 7.2 | 25 | 0.1 | 1955 | 1310 | 623 | 344 | 279 | 243 | 6.5 | 96 | NIL | 0.5 | 25 | 984 | 145
24.07.23 | 7.5 | 20 | 0 | 1627 | 1090 | 710 | 368 | 342 | 271 | 5.9 | 102 | NIL | 0.6 | 20 | 882 | 146
25.07.23 | 7.4 | 21 | 0 | 1522 | 1020 | 698 | 372 | 326 | 300 | 6.2 | 102 | NIL | 0.5 | 21 | 875 | 149
26.07.23 | 7.4 | 22 | 0 | 1403 | 940 | 706 | 364 | 342 | 290 | 5.9 | 87 | NIL | 0.5 | 22 | 960 | 152
27.07.23 | 7.3 | 21 | 0 | 1487 | 966 | 681 | 342 | 339 | 279 | 6.3 | 92 | NIL | 0.5 | 21 | 893 | 140
28.07.23 | 7.7 | 20 | 0.1 | 1343 | 900 | 648 | 300 | 348 | 254 | 6.9 | 104 | NIL | 0.5 | 20 | 888 | 134
29.07.23 | 7.9 | 18 | 0.1 | 1333 | 893 | 659 | 312 | 347 | 257 | 6.2 | 100 | NIL | 0.5 | 18 | 872 | 136
30.07.23 | 7.9 | 18 | 0.1 | 1333 | 893 | 659 | 312 | 347 | 257 | 6.2 | 100 | NIL | 0.5 | 18 | 886 | 149
31.07.23 | 7.5 | 48 | 0.1 | 1636 | 1096 | 668 | 321 | 347 | 272 | 6.1 | 104 | NIL | 0.5 | 48 | 893 | 139
MIN | 7 | 17 | 0 | 1333 | 893 | 549 | 300 | 205 | 142 | 5.8 | 87 | 0 | 0.4 | 17 | 754 | 130
MAX. | 7.9 | 28 | 0.5 | 2373 | 1590 | 710 | 377 | 355 | 321 | 10.5 | 120 | 0 | 0.8 | 70 | 984 | 169
AVG. | 7.5643 | 19 | 0.082143 | 1874.25 | 1253.6429 | 664.8571 | 349.9643 | 314.8929 | 260.2759 | 6.5714 | 97.6071 | 0 | 0.62593 | 26.8929 | 884.3571 | 149.25
No. of < Spec | 8 | -- | 23 | -- | -- | -- | -- | -- | -- | 2 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 18 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 28.5714 | -- | 82.1429 | -- | -- | -- | -- | -- | -- | 7.1429 | [5 empty] | --
% > Specs. | 0 | 64.2857 | 0 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0