## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.06.23 | 7.5 | 24 | 0.5 | 2047 | 1370 | 872 | 484 | 388 | 230 | 6.5 | 100 | NIL | 0.5 | 24 | 910 | 142
02.06.23 | 7.6 | 35 | 0 | 1940 | 1300 | 859 | 475 | 384 | 223 | 6.3 | 110 | NIL | 0.5 | 35 | 864 | 139
03.06.23 | 7.9 | 37 | 0 | 2000 | 1340 | 870 | 480 | 390 | 230 | 6.9 | 118 | NIL | 0.5 | 37 | 754 | 140
04.06.23 | 7.9 | 37 | 0 | 2000 | 1340 | 870 | 480 | 390 | 230 | 6.9 | 118 | NIL | 0.5 | 37 | 864 | 140
05.06.23 | 8 | 39 | 0.5 | 1492 | 1000 | 560 | 329 | 231 | 226 | 6.2 | 114 | NIL | 0.5 | 39 | 860 | 120
06.06.23 | 7.8 | 37 | 0.1 | 1350 | 905 | 517 | 315 | 202 | 230 | 6.5 | 120 | NIL | 0.4 | 37 | 873 | 122
07.06.23 | 8 | 35 | 0 | 1257 | 854 | 562 | 352 | 210 | 202 | 7 | 118 | NIL | 0.4 | 35 | 910 | 125
08.06.23 | 7.9 | 27 | 0 | 1704 | 1142 | 549 | 344 | 205 | 200 | 6.5 | 120 | NIL | 0.4 | 27 | 910 | 133
09.06.23 | 7.8 | 25 | 0 | 1737 | 1164 | 530 | 337 | 193 | 204 | 6.9 | 116 | NIL | 0.4 | 25 | 864 | 130
10.06.23 | 7.7 | 24 | 0 | 1750 | 1173 | 542 | 340 | 202 | 208 | 6 | 112 | NIL | 0.4 | 24 | 887 | 133
11.06.23 | 7.7 | 22 | 0 | 1750 | 1173 | 542 | 340 | 202 | 208 | 6 | 112 | NIL | 0.4 | 22 | 875 | 130
12.06.23 | 7.7 | 24 | 0 | 1552 | 1040 | 541 | 340 | 201 | 236 | 7.2 | 100 | NIL | 0.3 | 24 | 888 | 145
13.06.23 | 7.6 | 23 | 0 | 1611 | 1080 | 558 | 349 | 209 | 243 | 7.5 | 118 | NIL | 0.3 | 23 | 877 | 150
14.06.23 | 7.8 | 24 | 0.2 | 1573 | 1054 | 567 | 358 | 209 | 257 | 7 | 104 | NIL | 0.3 | 24 | 872 | 142
15.06.23 | 7.6 | 30 | 0.1 | 1950 | 1293 | 593 | 359 | 234 | 218 | 6.9 | 95 | NIL | 0.3 | 30 | 869 | 132
16.06.23 | 7.4 | 31 | 0.2 | 1966 | 1317 | 584 | 344 | 240 | 221 | 6 | 100 | NIL | 0.3 | 31 | 958 | 137
17.06.23 | 7.5 | 28 | 0.2 | 1952 | 1310 | 562 | 339 | 223 | 218 | 7 | 98 | NIL | 0.4 | 28 | 878 | 130
18.06.23 | 7.5 | 25 | 0.2 | 1952 | 1310 | 562 | 339 | 223 | 218 | 7 | 98 | NIL | 0.4 | 25 | 871 | 130
19.06.23 | 7.5 | 41 | 0 | 2000 | 1340 | 606 | 344 | 262 | 214 | 7 | 95 | NIL | 0.3 | 41 | 873 | 128
20.06.23 | 7.3 | 30 | 0.1 | 1630 | 1092 | 637 | 388 | 249 | 236 | 7.1 | 92 | NIL | 0.3 | 30 | 864 | 146
21.06.23 | 7.6 | 28 | 0 | 1896 | 1270 | 615 | 358 | 257 | 214 | 6.8 | 100 | NIL | 0.5 | 28 | 878 | 138
22.06.23 | 7.2 | 25 | 0.1 | 1955 | 1310 | 623 | 344 | 279 | 243 | 6.5 | 96 | NIL | 0.5 | 25 | 881 | 140
23.06.23 | 7.3 | 28 | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.06.23 | 7.6 | 37 | 0.3 | 1640 | 1093 | 589 | 348 | 241 | 240 | 6.5 | 92 | NIL | 0.6 | 37 | 982 | 130
25.06.23 | 7.6 | 33 | 0.3 | 1640 | 1093 | 589 | 348 | 241 | 240 | 6.5 | 92 | NIL | 0.6 | 33 | 875 | 137
26.06.23 | 7.7 | 35 | 0.1 | 1655 | 1109 | 579 | 351 | 228 | 243 | 6.7 | 89 | NIL | 0.7 | 35 | 960 | 139
27.06.23 | 7.1 | 30 | 0.1 | 1916 | 1284 | 612 | 345 | 267 | 237 | 5.9 | 90 | NIL | 0.7 | 30 | 893 | 141
28.06.23 | 7.4 | 28 | 0 | 1671 | 1120 | 603 | 242 | 361 | 229 | 6.3 | 82 | NIL | 0.8 | 28 | 888 | 146
29.06.23 | 7.6 | 27 | 0.1 | 1851 | 1240 | 621 | 351 | 270 | 243 | 6.9 | 84 | NIL | 0.8 | 27 | 872 | 151
30.06.23 | 7.7 | 28 | 0.1 | 1895 | 1270 | 634 | 369 | 265 | 240 | 7 | 90 | NIL | 0.8 | 28 | 893 | 146
MIN | 7.1 | 17 | 0 | 1257 | 854 | 517 | 242 | 193 | 142 | 5.8 | 82 | 0 | 0.3 | 22 | 754 | 120
MAX. | 8 | 28 | 0.5 | 2462 | 1650 | 894 | 519 | 390 | 257 | 10.5 | 120 | 0 | 0.8 | 55 | 984 | 151
AVG. | 7.6167 | 19 | 0.11 | 1793.1333 | 1201.2 | 628.0667 | 367.0333 | 261.0333 | 224.2903 | 6.67 | 102.7667 | 0 | 0.47586 | 30.8 | 887.5667 | 136.9
No. of < Spec | 6 | -- | 22 | -- | -- | -- | -- | -- | -- | 1 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 30 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 20 | -- | 73.3333 | -- | -- | -- | -- | -- | -- | 3.3333 | [5 empty] | --
% > Specs. | 0 | 100 | 0 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0