## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.04.22 | 8.4 | 20 | 0 | 2567 | 1720 | 794 | 458 | 336 | 232 | 5.4 | 105 | NIL | 0.2 | 20 | 910 | 168
02.04.22 | 7.1 | 20 | 0 | 2501 | 1680 | 785 | 449 | 336 | 224 | 7 | 110 | NIL | 0.2 | 20 | 864 | 170
03.04.22 | 7.1 | 20 | 0 | 2501 | 1680 | 785 | 449 | 336 | 224 | 7 | 110 | NIL | 0.2 | 20 | 864 | 170
04.04.22 | 8.1 | 20 | 0 | 2463 | 1650 | 752 | 441 | 311 | 377 | 5.8 | 102 | NIL | 0.2 | 20 | 864 | 165
05.04.22 | 8.3 | 19 | 0 | 2537 | 1700 | 743 | 445 | 298 | 369 | 6 | 110 | NIL | 0.2 | 19 | 887 | 160
06.04.22 | 8.2 | 18 | 0 | 2507 | 1680 | 722 | 437 | 285 | 355 | 6.2 | 102 | NIL | 0.2 | 18 | 864 | 150
07.04.22 | 7.5 | 18 | 0 | 2633 | 1764 | 714 | 428 | 286 | 312 | 6 | 100 | NIL | 0.2 | 18 | 887 | 152
08.04.22 | 7.5 | 21 | 0 | 2597 | 1740 | 735 | 433 | 302 | 327 | 6.6 | 102 | NIL | 0.2 | 21 | 887 | 150
09.04.22 | 7.5 | 20 | 0 | 2457 | 1780 | 769 | 462 | 307 | 363 | 6 | 112 | NIL | 0.2 | 20 | 864 | 172
10.04.22 | 7.5 | 20 | 0 | 2457 | 1780 | 769 | 462 | 307 | 363 | 6 | 112 | NIL | 0.2 | 20 | 864 | 172
11.04.22 | 7.7 | 20 | 0.1 | 2570 | 1792 | 756 | 458 | 298 | 334 | 6.3 | 102 | NIL | 0.2 | 20 | 878 | 156
12.04.22 | 7.7 | 23 | 0 | 2810 | 1883 | 790 | 491 | 299 | 348 | 6.9 | 109 | NIL | 0.2 | 23 | 875 | 166
13.04.22 | 7.7 | 20 | 0 | 2982 | 1998 | 794 | 500 | 294 | 363 | 7.2 | 113 | NIL | 0.2 | 20 | 877 | 169
14.04.22 | 8.4 | 30 | 0 | 3151 | 2098 | 802 | 517 | 285 | 377 | 7 | 120 | NIL | 0.2 | 30 | 881 | 176
15.04.22 | 7.9 | 28 | 0.2 | 2792 | 1810 | 772 | 492 | 280 | 340 | 6.2 | 110 | NIL | 0.2 | 28 | 869 | 160
16.04.22 | 8.2 | 35 | 0.2 | 2642 | 1770 | 790 | 500 | 290 | 348 | 6.6 | 100 | NIL | 0.2 | 35 | 958 | 165
17.04.22 | 8.2 | 35 | 0.2 | 2642 | 1770 | 790 | 500 | 290 | 348 | 6.6 | 100 | NIL | 0.2 | 35 | 958 | 165
18.04.22 | 7.8 | 41 | 0.5 | 3239 | 2170 | 920 | 546 | 374 | 356 | 6.2 | 109 | NIL | 0.2 | 41 | 893 | 178
19.04.22 | 7.9 | 35 | 0.2 | 3018 | 2022 | 911 | 542 | 369 | 327 | 6 | 100 | NIL | 0.2 | 35 | 873 | 170
20.04.22 | 7.7 | 40 | 0.1 | 2866 | 1920 | 882 | 563 | 319 | 327 | 6.1 | 107 | NIL | 0.2 | 40 | 864 | 168
21.04.22 | 7.858 | 58 | 0.5 | 3107 | 2082 | 903 | 580 | 801 | 298 | 6.4 | 102 | NIL | 0.2 | 58 | 878 | 179
22.04.22 | 7.9 | 42 | 0.1 | 2746 | 1840 | 882 | 567 | 315 | 312 | 6.1 | 100 | NIL | 0.2 | 42 | 890 | 167
23.04.22 | 7.9 | 79 | 0.5 | 3149 | 2110 | 899 | 584 | 315 | 327 | 6.6 | 100 | NIL | 0.2 | 79 | 984 | 170
24.04.22 | 7.9 | 79 | 0.5 | 3149 | 2110 | 899 | 584 | 315 | 327 | 6.6 | 100 | NIL | 0.2 | 79 | 984 | 170
25.04.22 | 7.6 | 65 | 0.2 | 2851 | 1910 | 890 | 580 | 310 | 305 | 6 | 104 | NIL | 0.2 | 65 | 878 | 162
26.04.22 | 7.8 | 42 | 0.1 | 2403 | 1610 | 899 | 601 | 298 | 327 | 6.9 | 113 | NIL | 0.2 | 42 | 880 | 170
27.04.22 | 7.7 | 39 | 0.1 | 2388 | 1600 | 882 | 588 | 294 | 348 | 7.1 | 100 | NIL | 0.2 | 39 | 880 | 165
28.04.22 | 8 | 28 | 0 | 2098 | 1398 | 878 | 580 | 298 | 334 | 7 | 109 | NIL | 0.2 | 28 | 889 | 166
29.04.22 | 8.3 | 22 | 0 | 2097 | 1405 | 869 | 567 | 302 | 305 | 6.6 | 118 | NIL | 0.2 | 22 | 881 | 169
30.04.22 | 8.2 | 18 | 0.1 | 2448 | 1640 | 752 | 550 | 202 | 312 | 4.2 | 109 | NIL | 0.2 | 18 | 890 | 159
MIN. | 7.1 | 17 | 0 | 2097 | 1398 | 714 | 428 | 202 | 142 | 5.8 | 100 | 0 | 0.2 | 18 | 864 | 150
MAX. | 8.4 | 28 | 0.5 | 3239 | 2170 | 920 | 601 | 801 | 377 | 10.5 | 120 | 0 | 0.2 | 79 | 984 | 179
AVG. | 7.8519 | 19 | 0.12 | 2678.9333 | 1803.7333 | 817.6 | 511.8 | 321.7333 | 321 | 6.3533 | 106.3333 | 0 | 0.2 | 32.5 | 890.5 | 165.9667
No. of < Spec | 2 | -- | 21 | -- | -- | -- | -- | -- | -- | 3 | -- | -- | -- | -- | -- | --
No. of > Spec | 9 | 18 | 0 | -- | 3 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 6.6667 | -- | 70 | -- | -- | -- | -- | -- | -- | 10 | [5 empty] | --
% > Specs. | 30 | 60 | 0 |  | 10 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0