## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | TSS | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | Max. 20 ppm | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-08-01 | 7.24 | 31 |  | NIL | 1746 | 1170 | 805 | 443 | 362 | 300 | 2.1 | - | NIL | 0.5 |  |  | 80
2024-08-02 | 7.88 | 14 |  | NIL | 1452 | 973 | 791 | 447 | 344 | 284 | 2.2 | - | NIL | 0.5 |  |  | 78
2024-08-03 | 7.7 | 12 |  | NIL | 1676 | 1123 | 798 | 447 | 351 | 288 | 2.1 | - | NIL | 0.5 |  |  | 75
2024-08-05 | 7.71 | 14 |  | NIL | 1805 | 1210 | 759 | 420 | 339 | 259 | 2.3 | - | NIL | 0.5 |  |  | 80
2024-08-06 | 7.98 | 12 |  | NIL | 2132 | 1429 | 773 | 429 | 344 | 259 | 2.5 | - | NIL | 0.5 |  |  | 75
2024-08-07 | 7.89 | 19 |  | NIL | 2566 | 1791 | 782 | 420 | 362 | 284 | 2.4 | - | NIL | 0.5 |  |  | 78
2024-08-08 | 7.54 | 12 |  | NIL | 2714 | 1819 | 814 | 434 | 380 | 275 | 2.5 | - | NIL | 0.5 |  |  | 76
2024-08-09 | 7.31 | 27 |  | NIL |  | 2060 | 805 | 425 | 380 | 284 | 2.4 | - | NIL | 0.5 |  |  | 78
2024-08-10 | 7.77 | 18 |  | 0.1 | 2718 | 1962 | 827 | 458 | 369 | 264 | 2.5 | - | NIL | 0.6 |  |  | 68
2024-08-12 | 7.85 | 25 |  | NIL | 3298 | 2210 | 1202 | 588 | 614 | 267 | 2.5 | - | NIL | 0.6 |  |  | 79
2024-08-13 | 7.26 | 23 |  | NIL | 3014 | 2020 | 1214 | 589 | 625 | 284 | 2.6 | - | NIL | 0.6 |  |  | 75
2024-08-14 | 7.74 | 25 |  | NIL | 2797 | 1874 | 1205 | 575 | 630 | 259 | 2.4 | - | NIL | 0.5 |  |  | 78
2024-08-16 | 7.47 | 37 |  | 0.1 | 2328 | 1560 | 1207 | 658 | 549 | 259 | 2.4 | - | NIL | 0.5 |  |  | 77
2024-08-17 | 7.51 | 37 |  | NIL | 2035 | 1364 | 1219 | 672 | 547 | 284 | 2.4 | - | NIL | 0.5 |  |  | 77
2024-08-20 | 7.58 | 31 |  | NIL | 1965 | 1317 | 1293 | 745 | 548 | 284 | 2.3 | - | NIL | 0.6 |  |  | 93
2024-08-21 | 7.25 | 32 |  | 0.1 | 1967 | 1318 | 777 | 483 | 294 | 284 | 2.3 | - | NIL | 0.6 |  |  | 95
2024-08-22 | 6.95 | 81 |  | 0.6 | 2908 | 1972 | 828 | 506 | 322 | 267 | 2.4 | - | NIL | 0.5 |  |  | 86
2024-08-23 | 7.6 | 36 |  | NIL | 1780 | 1193 | 805 | 570 | 235 | 251 | 2.4 | - | NIL | 0.5 |  |  | 81
2024-08-24 | 7.62 | 27 |  | NIL | 1861 | 1247 | 851 | 580 | 271 | 292 | 2.6 | - | NIL | 0.6 |  |  | 79
2024-08-27 | 7.26 | 35 |  | NIL | 1880 | 1260 | 764 | 529 | 235 | 295 | 2.5 | - | NIL | 0.5 |  |  | 78
2024-08-28 | 7.47 | 21 |  | NIL | 1964 | 1316 | 833 | 566 | 267 | 275 | 2.7 | - | NIL | 0.5 |  |  | 81
2024-08-29 | 7.4 | 23 |  | 0.5 | 1992 | 1335 | 842 | 589 | 308 | 275 | 2.3 | - | NIL | 0.5 |  |  | 85
2024-08-30 | 7.6 | 22 |  | 0.4 | 2279 | 1527 | 851 | 570 | 281 | 275 | 2.5 | - | NIL | 0.5 |  |  | 83
2024-08-31 | 7.6 | 23 |  | NIL | 1961 | 1314 | 810 | 437 | 373 | 251 | 2.7 | - | NIL | 0.6 |  |  | 93
2024-09-02 | 7.11 | 16 |  | 0.6 | 1843 | 1235 | 843 | 767 | 76 | 228 | 2.6 | - | NIL | 0.5 |  |  | 84
2024-09-03 | 7 | 22 |  | NIL | 2032 | 1362 | 838 | 356 | 482 | 483 | 2.8 | - | NIL | 0.6 |  |  | 80
2024-09-04 | 7.02 | 30 |  | 1 | 2608 | 1748 | 970 | 427 | 543 | 203 | 2.6 | - | NIL | 0.6 |  |  | 91
2024-09-05 | 6.96 | 32 |  | NIL | 2247 | 1506 | 940 | 417 | 523 | 227 | 2.8 | - | NIL | 0.6 |  |  | 85
2024-09-06 | 7.23 | 36 |  | NIL | 2925 | 1960 | 889 | 523 | 366 | 252 | 3.3 | - | NIL | 0.6 |  |  | 89
07.09.24 | 7.17 | 20 |  | 0.2 | 2383 | 1597 | 904 | 508 | 396 | 236 | 3.2 | - | NIL | 0.6 |  |  | 90
09.09.24 | 7.38 | 21 |  | 0.7 | 2155 | 1444 | 909 | 472 | 437 | 252 | 3.1 | - | NIL | 0.6 |  |  | 83
10.09.24 | 7.54 | 22 |  | NIL | 1536 | 1029 | 864 | 447 | 417 | 244 | 2.9 | - | NIL | 0.6 |  |  | 77
11.09.24 | 7.44 | 12 |  | NIL | 1934 | 1296 | 838 | 432 | 406 | 236 | 3.1 | - | NIL | - |  |  | 81
12.09.24 | 7.16 | 16 |  | 0.6 | 2024 | 1356 | 899 | 437 | 462 | 226 | 3 | - | NIL | 0.6 |  |  | 79
13.09.24 | 7.31 | 22 |  | 0.2 | 1516 | 1016 | 889 | 427 | 462 | 218 | 3.1 | - | NIL | 0.5 |  |  | 84
2024-09-14 | 7.3 | 18 |  | NIL | 2270 | 1521 | 914 | 442 | 472 | 240 | 3.3 | - | NIL | 0.5 |  |  | 80
2024-09-17 | 8.23 | 90 |  | NIL | 1073 | 719 | 828 | 737 | 91 | 391 | 3.2 | - | NIL | 0.5 |  |  | 81
2024-09-18 | 7.7 | 86 |  | 0.2 | 1110 | 744 | 848 | 332 | 516 | 211 | 3 | - | NIL | 0.5 |  |  | 79
19.09.24 | 7.6 | 35 |  | 0.4 | 1144 | 767 | 749 | 403 | 346 | 192 | 3.1 | - | NIL | 0.5 |  |  | 83
2024-09-20 | 7.02 | 33 |  | 0.2 | 1446 | 969 | 758 | 389 | 369 | 187 | 3.3 | - | NIL | 0.5 |  |  | 78
21.09.24 | 7.76 | 20 |  | NIL | 1347 | 903 | 728 | 385 | 343 | 171 | 3.5 | - | NIL | 0.5 |  |  | 80
23.09.24 | 7.69 | 22 |  | 0.5 | 1608 | 1078 | 696 | 348 | 348 | 178 | 3.3 | - | NIL | 0.5 |  |  | 80
2024-09-24 | 7.15 | 20 |  | NIL | 1774 | 1189 | 668 | 339 | 329 | 186 | 3.3 | - | NIL | 0.5 |  |  | 80
25.09.24 | 7.59 | 30 |  | 0.5 | 1613 | 1081 | 724 | 380 | 344 | 203 | 3.5 | - | NIL | 0.5 |  |  | 81
2024-09-26 | 7.29 | 30 |  | 0.8 | 1613 | 1081 | 701 | 371 | 330 | 186 | 3.2 | - | NIL | 0.5 |  |  | 85
2024-09-27 | 7.2 | 23 |  | NIL | 1805 | 1210 | 665 | 324 | 341 | 175 | 3.1 | - | NIL | 0.5 |  |  | 82
2024-09-28 | 6.97 | 15 |  | NIL | 1740 | 1166 | 661 | 333 | 328 | 167 | 3.3 | - | NIL | 0.5 |  |  | 79
30.09.24 | 6.9 | 18 |  | 0.2 | 1812 | 1214 | 665 | 328 | 337 | 160 | 3.1 | - | NIL | 0.5 |  |  | 81
2024-10-01 | 7.25 | 18 |  | 0.6 | 1882 | 1261 | 858 | 496 | 362 | 255 | 2.7 | - | NIL | 0.6 |  |  | 83
2024-10-02 | 7.75 | 16 |  | 0.6 | 1844 | 1236 | 844 | 487 | 357 | 248 | 2.6 | - | NIL | 0.6 |  |  | 85
03.10.24 | 7.15 | 18 |  | 0.5 | 1502 | 1007 | 835 | 473 | 362 | 233 | 2.5 | - | NIL | 0.5 |  |  | 81
04.10.24 | 7.66 | 24 |  | 0.5 | 1762 | 1181 | 844 | 478 | 366 | 240 | 2.4 | - | NIL | 0.5 |  |  | 83
2024-10-05 | 7.37 | 20 |  | 0.5 | 1825 | 1223 | 640 | 469 | 171 | 240 | 2.5 | - | NIL | 0.5 |  |  | 87
2024-10-07 | 7.53 | 22 |  | 0.6 | 1582 | 1060 | 691 | 436 | 255 | 226 | 2.3 | - | NIL | 0.6 |  |  | 86
08.10.24 | 7.82 | 51 |  | 0.8 | 1679 | 1125 | 655 | 429 | 226 | 262 | 2.4 | - | NIL | 0.5 |  |  | 85
09.10.24 | 7.66 | 40 |  | NIL | 1743 | 1168 | 660 | 420 | 240 | 240 | 2.1 | - | NIL | 0.5 |  |  | 82
10.10.24 | 7.92 | 35 |  | NIL | 1968 | 1319 | 673 | 307 | 366 | 247 | 2.2 | - | NIL | 0.5 |  |  | 85
11.10.24 | 7.85 | 33 |  | NIL | 2192 | 1469 | 664 | 294 | 370 | 212 | 2.1 | - | NIL | 0.5 |  |  | 79
12.10.24 | 7.83 | 28 |  | 0.5 | 2674 | 1792 | 669 | 289 | 380 | 247 | 2.2 | - | NIL | 0.5 |  |  | 81
2024-10-14 | 6.83 | 28 |  | 1 | 2573 | 1724 | 678 | 325 | 353 | 306 | 2.3 | - | NIL | 0.5 |  |  | 82
15.10.24 | 6.95 | 29 |  | 1 | 2984 | 1999 | 687 | 334 | 353 | 298 | 2.1 | - | NIL | 0.5 |  |  | 81
16.10.24 | 7.48 | 24 |  | 0.2 | 2779 | 1862 | 678 | 330 | 348 | 291 | 2.2 | - | NIL | 0.5 |  |  | 86
17.10.24 | 7.85 | 19 |  | NIL | 2331 | 1562 | 655 | 325 | 330 | 277 | 2.3 | - | NIL | 0.5 |  |  | 83
18.10.24 | 7.43 | 18 |  | NIL | 2553 | 1711 | 659 | 339 | 320 | 277 | 2.1 | - | NIL | 0.5 |  |  | 82
19.10.24 | 7.36 | 22 |  | 0.8 | 2764 | 1852 | 668 | 336 | 332 | 284 | 2.2 | - | NIL | 0.5 |  |  | 79
21.10.24 | 7.67 | 24 |  | 0.6 | 2496 | 1672 | 696 | 292 | 404 | 370 | 4.3 | - | NIL | 0.6 |  |  | 80
22.10.24 | 7.35 | 30 |  | 0.4 | 2385 | 1598 | 770 | 362 | 408 | 335 | 3.5 | - | NIL | 0.6 |  |  | 82
23.10.24 | 7.48 | 21 |  | 0.4 | 2714 | 1819 | 789 | 371 | 418 | 364 | 3.5 | - | NIL | 0.5 |  |  | 86
24.10.24 | 7.65 | 18 |  | NIL | 2577 | 1727 | 759 | 253 | 506 | 349 | 3.4 | - | NIL | 0.5 |  |  | 80
25.10.24 | 6.96 | 21 |  | 0.4 | 2865 | 1920 | 768 | 366 | 402 | 364 | 3.5 | - | NIL | 0.5 |  |  | 86
26.10.24 | 7.39 | 37 |  | 0.8 | 2463 | 1650 | 764 | 362 | 402 | 357 | 3.4 | - | NIL | 0.5 |  |  | 80
28.10.24 | STOP
29.10.24 | STOP
30.10.24 | 8.32 | 69 |  | NIL | 1597 | 1070 | 678 | 325 | 353 | 306 | 3.3 | - | NIL | 0.5 |  |  | 86
31.10.24 | 7.01 | 65 |  | NIL | 1825 | 1223 | 657 | 318 | 339 | 335 | 3.3 | - | NIL | 0.5 |  |  | 84
04.11.24 | 7.42 | 60 |  | 1 | 2328 | 1560 | 691 | 390 | 301 | 387 | 3.2 | - | NIL | 0.5 |  |  | 83
05.11.24 | 7.86 | 62 |  | NIL | 2422 | 1623 | 702 | 405 | 297 | 320 | 3.1 | - | NIL | 0.5 |  |  | 81
06.11.24 | 7.65 | 35 |  | NIL | 2455 | 1645 | 706 | 401 | 305 | 306 | 3.2 | - | NIL | 0.5 |  |  | 85
07.11.24 | 7.68 | 36 |  | NIL | 2813 | 1885 | 708 | 396 | 312 | 313 | 3.3 | - | NIL | 0.5 |  |  | 84
08.11.24 | 7.82 | 55 |  | 0.9 | 2913 | 1952 | 726 | 409 | 317 | 306 | 3.2 | - | NIL | 0.5 |  |  | 86
09.11.24 | 8.51 | 53 |  | 0.9 | 3268 | 2190 | 968 | 594 | 374 | 313 | 3.3 | - | NIL | 0.5 |  |  | 85
11.11.24 | 7.49 | 43 |  | NIL | 3283 | 2200 | 906 | 573 | 333 | 306 | 3.1 | - | NIL | 0.5 |  |  | 83
12.11.24 | 7.1 | 30 |  | NIL | 3402 | 2280 | 911 | 581 | 330 | 298 | 3.2 | - | NIL | 0.5 |  |  | 36
13.11.24 | 6.93 | 38 |  | 0.4 | 3671 | 2460 | 895 | 562 | 333 | 334 | 3.1 | - | NIL | 0.5 |  |  | 83
14.11.24 | 7.83 | 37 |  | 0.1 | 3179 | 2130 | 853 | 541 | 312 | 306 | 3.2 | - | NIL | 0.5 |  |  | 80
15.11.24 | 7.56 | 37 |  | NIL | 2850 | 1910 | 844 | 499 | 345 | 291 | 3.1 | - | NIL | 0.5 |  |  | 82
16.11.24 | 7.8 | 37 |  | NIL | 2965 | 1987 | 832 | 508 | 324 | 291 | 3.1 | - | NIL | 0.5 |  |  | 81
18.11.24 | 7.8 | 26 |  | NIL | 3104 | 2080 | 853 | 499 | 354 | 298 | 3.2 | - | NIL | 0.5 |  |  | 83
19.11.24 | 8.16 | 30 |  | NIL | 3000 | 2010 | 911 | 503 | 408 | 306 | 3.3 | - | NIL | 0.5 |  |  | 82
20.11.24 | 7.01 | 29 |  | 0.9 | 3268 | 2190 | 903 | 516 | 387 | 327 | 3.4 | - | NIL | 0.5 |  |  | 83
21.11.24 | 7.22 | 30 |  | NIL | 2870 | 1923 | 915 | 500 | 415 | 306 | 3.5 | - | NIL | 0.5 |  |  | 86
22.11.24 | 6.36 | 28 |  | 0.9 | 3164 | 2120 | 907 | 512 | 395 | 320 | 3.2 | - | NIL | 0.5 |  |  | 80
23.11.24 | 7.7 | 37 |  | 0.3 | 3104 | 2080 | 920 | 512 | 408 | 313 | 3.5 | - | NIL | 0.5 |  |  | 84
25.11.24 | 7.84 | 30 |  | NIL | 2885 | 1993 | 920 | 512 | 408 | 313 | 3.4 | - | NIL | 0.5 |  |  | 80
26.11.24 | 7.01 | 25 |  | 0.9 | 2985 | 2000 | 924 | 517 | 407 | 320 | 3.5 | - | NIL | 0.5 |  |  | 82
27.11.24 | 8.15 | 25 |  | 0.1 | 2764 | 1852 | 903 | 504 | 399 | 306 | 3.4 | - | NIL | 0.5 |  |  | 82
28.11.24 | 8.19 | 25 |  | 0.5 | 3014 | 2020 | 932 | 525 | 407 | 327 | 3.5 | - | NIL | 0.5 |  |  | 86
29.11.24 | 7.76 | 28 |  | NIL | 2758 | 1848 | 907 | 504 | 403 | 335 | 3.4 | - | NIL | 0.5 |  |  | 83
30.11.24 | 7.71 | 25 |  | NIL | 2565 | 1719 | 916 | 517 | 399 | 313 | 3.5 | - | NIL | 0.5 |  |  | 80
02.12.24 | 7.76 | 28 |  | NIL | 2513 | 1684 | 916 | 517 | 399 | 313 | 3.2 | - | NIL | 0.5 |  |  | 82
03.12.24 | 7.21 | 20 |  | 0.7 | 2441 | 1636 | 912 | 509 | 403 | 306 | 3.4 | - | NIL | 0.5 |  |  | 80
04.12.24 | 7.6 | 20 |  | NIL | 2628 | 1761 | 920 | 517 | 403 | 306 | 3.3 | - | NIL | 0.5 |  |  | 85
05.12.24 | 7.78 | 24 |  | NIL | 2513 | 1684 | 929 | 530 | 399 | 305 | 3.5 | - | NIL | 0.5 |  |  | 80
06.12.24 | 7.31 | 35 |  | NIL | 2634 | 1765 | 924 | 522 | 402 | 306 | 3.3 | - | NIL | 0.5 |  |  | 85
07.12.24 | 7.1 | 32 |  | NIL | 2464 | 1651 | 874 | 475 | 399 | 291 | 3.5 | - | NIL | 0.4 |  |  | 92
09.12.24 | 7.06 | 21 |  | 1 | 2776 | 1860 | 869 | 462 | 407 | 291 | 3.1 | - | NIL | 0.5 |  |  | 89
10.12.24 | 7.2 | 25 |  | NIL | 2391 | 1602 | 874 | 470 | 404 | 306 | 3.2 | - | NIL | 0.5 |  |  | 83
11.12.24 | 6.95 | 28 |  | NIL | 2752 | 1844 | 890 | 475 | 415 | 313 | 3.1 | - | NIL | 0.5 |  |  | 82
12.12.24 | 7.66 | 28 |  | NIL | 2448 | 1640 | 886 | 466 | 420 | 306 | 3.2 | - | NIL | 0.5 |  |  | 81
13.12.24 | 7.36 | 36 |  | 0.6 | 2447 | 1640 | 895 | 470 | 425 | 313 | 3.1 | - | NIL | 0.5 |  |  | 84
14.12.24 | 7.05 | 41 |  | 0.5 | 2734 | 1832 | 873 | 466 | 407 | 306 | 3.3 | - | NIL | 0.5 |  |  | 81
16.12.24 | 6.87 | 25 |  | NIL | 2782 | 1864 | 911 | 482 | 429 | 313 | 3.2 | - | NIL | 0.5 |  |  | 89
17.12.24 | 7.46 | 29 |  | NIL | 3223 | 2160 | 906 | 475 | 431 | 306 | 3.5 | - | NIL | 0.5 |  |  | 87
18.12.24 | 7.1 | 35 |  | 0.4 | 3208 | 2150 | 915 | 480 | 435 | 307 | 3.4 | - | NIL | 0.5 |  |  | 88
19.12.24 | 7.15 | 36 |  | 0.7 | 3089 | 2070 | 907 | 478 | 429 | 291 | 3.7 | - | NIL | 0.5 |  |  | 80
20.12.24 | 7.89 | 28 |  | NIL | 3179 | 2130 | 919 | 483 | 436 | 313 | 3.4 | - | NIL | 0.5 |  |  | 85
21.12.24 | 6.76 | 30 |  | NIL | 2953 | 1979 | 899 | 478 | 421 | 291 | 3.4 | - | NIL | 0.5 |  |  | 80
23.12.24 | 6.95 | 30 |  | NIL | 3716 | 2490 | 906 | 461 | 445 | 320 | 3.5 | - | NIL | 0.5 |  |  | 85
24.12.24 | 7.43 | 25 |  | NIL | 2443 | 1637 | 877 | 457 | 420 | 327 | 3.4 | - | NIL | 0.5 |  |  | 80
25.12.24 | 7.14 | 24 |  | 0.7 | 2864 | 1919 | 902 | 465 | 437 | 320 | 3.3 | - | NIL | 0.5 |  |  | 82
26.12.24 | 7.42 | 28 |  | NIL | 2647 | 1774 | 910 | 457 | 453 | 327 | 3.5 | - | NIL | 0.5 |  |  | 82
27.12.24 | 7.34 | 32 |  | NIL | 2861 | 1917 | 918 | 465 | 453 | 320 | 3.2 | - | NIL | 0.5 |  |  | 85
28.12.24 | 7.61 | 18 |  | NIL | 2520 | 1689 | 869 | 479 | 390 | 313 | 3.4 | - | NIL | 0.5 |  |  | 82
30.12.24 | 6.69 | 22 |  | NIL | 2628 | 1761 | 901 | 505 | 396 | 313 | 3.5 | - | NIL | 0.5 |  |  | 89
31.12.24 | 7.46 | 22 |  | NIL | 2928 | 1962 | 933 | 488 | 445 | 335 | 3.8 | - | NIL | 0.5 |  |  | 84
01.01.25 | 6.89 | 25 |  | NIL | 2595 | 1739 | 1003 | 533 | 470 | 364 | 4.2 | - | NIL | 0.4 |  |  | 89
02.01.25 | 7.1 | 25 |  | 0.6 | 2764 | 1852 | 1012 | 537 | 475 | 371 | 4.3 | - | NIL | 0.5 |  |  | 88
03.01.25 | 7.1 | 25 |  | 0.5 | 2928 | 1962 | 1017 | 542 | 475 | 386 | 4.4 | - | NIL | 0.4 |  |  | 86
04.01.25 | 7.02 | 22 |  | NIL | 3238 | 2170 | 1012 | 533 | 479 | 366 | 4.3 | - | NIL | 0.5 |  |  | 84
06.01.25 | 6.86 | 24 |  | NIL | 3164 | 2120 | 1052 | 533 | 519 | 373 | 4.3 | - | NIL | 0.4 |  |  | 88
07.01.25 | 6.85 | 20 |  | 0.8 | 3060 | 2050 | 1021 | 537 | 484 | 359 | 4.5 | - | NIL | 0.5 |  |  | 81
08.01.25 | 6.15 | 29 |  | 1 | 3044 | 2040 | 1030 | 533 | 497 | 366 | 4.2 | - | NIL | 0.4 |  |  | 90
09.01.25 | 7.39 | 21 |  | 0.4 | 3104 | 2080 | 1021 | 542 | 479 | 380 | 4.4 | - | NIL | 0.5 |  |  | 86
10.01.25 | 6.98 | 23 |  | NIL | 3029 | 2030 | 1026 | 506 | 520 | 366 | 4.3 | - | NIL | 0.5 |  |  | 83
11.01.25 | 7.6 | 21 |  | NIL | 3223 | 2160 | 1035 | 543 | 492 | 359 | 4.3 | - | NIL | 0.5 |  |  | 81
13.01.25 | 7.85 | 18 |  | NIL | 2910 | 1950 | 1248 | 568 | 680 | 366 | 4.2 | - | NIL | 0.4 |  |  | 83
15.01.25 | 7.11 | 23 |  | 1 | 2619 | 1755 | 1267 | 575 | 692 | 366 | 4.2 | - | NIL | 0.5 |  |  | 83
16.01.25 | 7.13 | 35 |  | 1 | 2795 | 1873 | 1253 | 557 | 696 | 359 | 4.3 | - | NIL | 0.5 |  |  | 78
17.01.25 | 7.73 | 28 |  | NIL | 2741 | 1837 | 1244 | 561 | 683 | 359 | 4.1 | - | NIL | 0.5 |  |  | 85
18.01.25 | 7.12 | 38 |  | NIL | 2607 | 1747 | 1216 | 557 | 659 | 366 | 4.2 | - | NIL | 0.5 |  |  | 83
20.01.25 | 6.68 | 33 |  | 0.6 | 3029 | 2030 | 1230 | 561 | 669 | 359 | 4 | - | NIL | 0.5 |  |  | 83
21.01.25 | 7.61 | 32 |  | NIL | 2500 | 1675 | 1253 | 571 | 682 | 380 | 4.3 | - | NIL | 0.6 |  |  | 85
22.01.25 | 7.78 | 30 |  | NIL | 2753 | 1845 | 1262 | 566 | 696 | 387 | 4.1 | - | NIL | 0.5 |  |  | 82
23.01.25 | 7.08 | 25 |  | NIL | 3044 | 2040 | 1308 | 580 | 728 | 395 | 4.3 | - | NIL | 0.6 |  |  | 92
24.01.25 | 7.46 | 30 |  | 1 | 3029 | 2030 | 1313 | 571 | 742 | 380 | 4.2 | - | NIL | 0.5 |  |  | 86
25.01.25 | 7.45 | 31 |  | NIL | 2871 | 1924 | 1349 | 581 | 768 | 373 | 4.1 | - | NIL | 0.6 |  |  | 87
27.01.25 | 7.49 | 26 |  | NIL | 2589 | 1735 | 1320 | 586 | 734 | 384 | 4.3 | - | NIL | 0.6 |  |  | 86
28.01.25 | 7.44 | 28 |  | 0.5 | 2947 | 1975 | 1310 | 576 | 734 | 380 | 5.1 | - | NIL | 0.5 |  |  | 89
29.01.25 | 7.12 | 28 |  | 1 | 2973 | 1991 | 1325 | 595 | 730 | 388 | 5.2 | - | NIL | 0.6 |  |  | 88
30.01.25 | 7.82 | 32 |  | 0.7 | 3731 | 2500 | 1488 | 624 | 864 | 395 | 5.4 | - | NIL | 0.7 |  |  | 65
31.01.25 | 7.45 | 41 |  | 1 | 3328 | 2230 | 1498 | 629 | 869 | 380 | 5.2 | - | NIL | 0.5 |  |  | 39
01.02.25 | 7.16 | 42 |  | NIL | 3179 | 2130 | 1394 | 586 | 808 | 394 | 5.4 | - | NIL | 0.6 |  |  | 75
03.02.25 | 7.86 | 30 |  | NIL | 2892 | 1938 | 1412 | 761 | 651 | 369 | 5.2 | - | NIL | 0.5 |  |  | 70
04.02.25 | 7.43 | 32 |  | NIL | 2634 | 1765 | 1465 | 795 | 670 | 38 | 5.4 | - | NIL | 0.6 |  |  | 73
05.02.25 | 7.35 | 20 |  | NIL | 2782 | 1864 | 1452 | 777 | 675 | 366 | 5.3 | - | NIL | 0.5 |  |  | 70
06.02.25 | 7.25 | 25 |  | 0.7 | 2850 | 1910 | 1470 | 768 | 702 | 394 | 5.8 | - | NIL | 0.6 |  |  | 75
07.02.25 | 7.06 | 37 |  | 0.5 | 2942 | 1971 | 1479 | 764 | 715 | 359 | 5.4 | - | NIL | 0.5 |  |  | 73
08.02.25 | 0.5 | 28 |  | NIL | 2697 | 1807 | 1456 | 755 | 701 | 366 | 5.2 | - | NIL | 0.5 |  |  | 72
10.02.25 | 7 | 30 |  | 0.2 | 2426 | 1626 | 1492 | 777 | 715 | 387 | 5.6 | - | NIL | 0.5 |  |  | 74
11.02.25 | 7.01 | 22 |  | 0.4 | 2508 | 1681 | 1208 | 719 | 489 | 373 | 5.9 | - | NIL | 0.6 |  |  | 70
12.02.25 | 7.57 | 23 |  | 0.6 | 2485 | 1665 | 1221 | 733 | 488 | 380 | 5.7 | - | NIL | 0.5 |  |  | 80
13.02.25 | 7.44 | 18 |  | 0.7 | 2280 | 1528 | 1208 | 719 | 489 | 394 | 5.5 | - | NIL | 0.5 |  |  | 85
14.02.25 | 7.16 | 34 |  | 0.6 | 2103 | 1409 | 1199 | 710 | 489 | 380 | 5.5 | - | NIL | 0.5 |  |  | 81
15.02.25 | 7.03 | 39 |  | 0.6 | 2508 | 1547 | 1208 | 724 | 484 | 387 | 5.7 | - | NIL | 0.5 |  |  | 84
17.02.25 | 7.26 | 36 |  | 0.8 | 2479 | 1661 | 1212 | 719 | 493 | 380 | 5 | - | NIL | 0.5 |  |  | 86
18.02.25 | 6.78 | 48 |  | 0.6 | 2759 | 1849 | 1225 | 741 | 484 | 373 | 5.5 | - | NIL | 0.5 |  |  | 81
19.02.25 | 7.55 | 40 |  | 0.5 | 2347 | 1573 | 1190 | 785 | 405 | 394 | 5.8 | - | NIL | 0.5 |  |  | 85
20.02.25 | 7.41 | 24 |  | NIL | 2295 | 1538 | 1166 | 771 | 395 | 359 | 5.5 | - | NIL | 0.4 |  |  | 77
21.02.25 | 7.38 | 28 |  | NIL | 2368 | 1587 | 1180 | 762 | 418 | 380 | 5.2 | - | NIL | 0.5 |  |  | 82
22.02.25 | 7.26 | 29 |  | NIL | 2231 | 1495 | 1150 | 751 | 399 | 366 | 5.4 | - | NIL | 0.4 |  |  | 79
24.02.25 | 6.86 | 26 |  | 1 | 2167 | 1452 | 1095 | 727 | 368 | 359 | 5.3 | - | NIL | 0.4 |  |  | 77
25.02.25 | 7.17 | 29 |  | 0.6 | 2171 | 1455 | 1063 | 690 | 373 | 388 | 5 | - | NIL | 0.5 |  |  | 70
27.02.25 | 7.7 | 24 |  | 0.8 | 2114 | 1417 | 1032 | 652 | 380 | 345 | 5.5 | - | NIL | 0.4 |  |  | 75
28.02.25 | 7.7 | 23 |  | NIL | 2610 | 1749 | 1028 | 657 | 371 | 361 | 5.2 | - | NIL | 0.5 |  |  | 73
01.03.25 | 7.21 | 25 |  | NIL | 3037 | 2035 | 1035 | 687 | 348 | 323 | 5.2 | - | NIL | 0.5 |  |  | 76
03.03.25 | 7.6 | 30 |  | NIL | 2756 | 1847 | 1011 | 626 | 385 | 364 | 5.1 | - | NIL | - |  |  | 74
04.03.25 | 7.26 | 29 |  | NIL | 2855 | 1913 | 1024 | 639 | 385 | 373 | 5.3 | - | NIL | 0.6 |  |  | 75
05.03.25 | 7.42 | 25 |  | 0.1 | 2802 | 1878 | 1037 | 635 | 402 | 382 | 5 | - | NIL | 0.5 |  |  | 78
06.03.25 | 7.06 | 21 |  | 1 | 3147 | 2109 | 1106 | 613 | 493 | 355 | 4.8 | - | NIL | 0.6 |  |  | 72
07.03.25 | 6.82 | 35 |  | NIL | 3208 | 2150 | 1115 | 613 | 502 | 373 | 4.3 | - | NIL | 0.5 |  |  | 70
08.03.25 | 6.56 | 28 |  | NIL | 2938 | 1969 | 1060 | 644 | 416 | 371 | 4.5 | - | NIL | 0.5 |  |  | 72
10.03.25 | 7.01 | 22 |  | NIL | 2962 | 1985 | 1064 | 657 | 407 | 373 | 4.4 | - | NIL | 0.6 |  |  | 75
11.03.25 | 7.28 | 24 |  | NIL | 3119 | 2090 | 990 | 660 | 330 | 355 | 4.2 | - | NIL | 0.5 |  |  | 78
12.03.25 | 7.05 | 24 |  | 1 | 2411 | 1616 | 1012 | 659 | 353 | 364 | 4.4 | - | NIL | 0.5 |  |  | 72
13.03.25 | 7.02 | 28 |  | 1 | 2546 | 1706 | 1065 | 660 | 405 | 382 | 4.2 | - | NIL | 0.9 |  |  | 70
15.03.25 | 7.25 | 29 |  | 1 | 2079 | 1393 | 1052 | 662 | 390 | 355 | 4.1 | - | NIL | 0.5 |  |  | 70
17.03.25 | 7.14 | 22 |  | 0.8 | 2573 | 1724 | 946 | 528 | 418 | 364 | 4.2 | - | NIL | 0.6 |  |  | 72
18.03.25 | 7.46 | 26 |  | 0.5 | 1964 | 1316 | 968 | 537 | 431 | 382 | 4.3 | - | NIL | 0.5 |  |  | 76
19.03.25 | 7.09 | 19 |  | NIL | 1943 | 1302 | 998 | 575 | 423 | 409 | 4.6 | - | NIL | 0.6 |  |  | 73
20.03.25 | 7.05 | 24 |  | NIL | 2000 | 1340 | 994 | 580 | 414 | 400 | 4.3 | - | NIL | 0.6 |  |  | 72
21.03.25 | 7.33 | 30 |  | 0.5 | 1940 | 1300 | 994 | 575 | 419 | 391 | 4.5 | - | NIL | 0.5 |  |  | 70
22.03.25 | 7.08 | 30 |  | 0.5 | 2123 | 1423 | 998 | 584 | 414 | 382 | 4.4 | - | NIL | 0.5 |  |  | 73
24.03.25 | 7.71 | 32 |  | 0.5 | 2201 | 1475 | 994 | 575 | 419 | 382 | 4.2 | - | NIL | 0.5 |  |  | 72
25.03.25 | 7.24 | 25 |  | 0.5 | 2384 | 1597 | 925 | 529 | 396 | 400 | 4.3 | - | NIL | 0.5 |  |  | 70
26.03.25 | 7.01 | 20 |  | 0.5 | 2708 | 1815 | 957 | 547 | 410 | 377 | 4.5 | - | NIL | 0.5 |  |  | 77
27.03.25 | 7.58 | 26 |  | NIL | 2597 | 1740 | 966 | 552 | 414 | 391 | 4.5 | - | NIL | 0.5 |  |  | 75
28.03.25 | 7.03 | 33 |  | 0.5 | 2550 | 1709 | 989 | 566 | 423 | 404 | 4.4 | - | NIL | 0.5 |  |  | 72
29.03.25 | 7.7 | 26 |  | 0.6 | 2387 | 1599 | 971 | 502 | 469 | 384 | 4.3 | - | NIL | 0.5 |  |  | 72
31.03.25 | 7.6 | 26 |  | NIL | 2420 | 1622 | 929 | 483 | 446 | 377 | 4.5 | - | NIL | 0.5 |  |  | 79
01.04.25 | 7.09 | 24 |  | 0.7 | 2405 | 1612 | 883 | 497 | 386 | 236 | 3.2 | - | NIL | 0.5 |  |  | 83
02.04.25 | 7.64 | 15 |  | 0.4 | 2528 | 1694 | 920 | 483 | 437 | 252 | 3.3 | - | NIL | 0.4 |  |  | 77
03.04.25 | 7.14 | 19 |  | NIL | 2860 | 1916 | 966 | 506 | 460 | 276 | 3.1 | - | NIL | 0.5 |  |  | 75
04.04.25 | 7.14 | 18 |  | NIL | 3030 | 2030 | 975 | 515 | 460 | 260 | 3.2 | - | NIL | 0.4 |  |  | 78
05.04.25 | 7.17 | 17 |  | 1 | 2803 | 1878 | 966 | 529 | 437 | 276 | 3.3 | - | NIL | 0.5 |  |  | 76
07.04.25 | 7.22 | 17 |  | 0.8 | 2530 | 1695 | 1021 | 515 | 506 | 260 | 3.2 | - | NIL | 0.5 |  |  | 77
08.04.25 | 6.91 | 22 |  | 0.9 | 2634 | 1765 | 1104 | 621 | 483 | 276 | 3.4 | - | NIL | 0.5 |  |  | 80
09.04.25 | 7.43 | 18 |  | 0.2 | 2446 | 1639 | 1081 | 616 | 465 | 252 | 3.5 | - | NIL | 0.5 |  |  | 72
10.04.25 | 7.41 | 25 |  | NIL | 2459 | 1648 | 1104 | 621 | 483 | 260 | 3.6 | - | NIL | 0.6 |  |  | 74
11.04.25 | 6.96 | 20 |  | NIL | 2968 | 1989 | 1095 | 630 | 465 | 252 | 3.4 | - | NIL | 0.5 |  |  | 79
12.04.25 | 7.57 | 18 |  | NIL | 3044 | 2040 | 1109 | 621 | 488 | 276 | 3.1 | - | NIL | 0.5 |  |  | 83
14.04.25 | 7.45 | 22 |  | 0.5 | 2231 | 1495 | 1090 | 593 | 497 | 352 | 3 | - | NIL | 0.5 |  |  | 78
15.04.25 | 7.95 | 26 |  | 0.5 | 2197 | 1472 | 1104 | 598 | 506 | 268 | 4 | - | NIL | 0.5 |  |  | 76
16.04.25 | 7.02 | 22 |  | 0.5 | 2697 | 1807 | 1095 | 589 | 506 | 252 | 4.2 | - | NIL | 0.5 |  |  | 78
17.04.25 | 7.13 | 15 |  | 0.1 | 2292 | 1536 | 1118 | 580 | 538 | 276 | 4.6 | - | NIL | 0.5 |  |  | 79
18.04.25 | 6.79 | 16 |  | NIL | 2296 | 1538 | 1109 | 561 | 548 | 263 | 4.2 | - | NIL | 0.5 |  |  | 75
19.04.25 | 6.41 | 20 |  | 0.1 | 2310 | 1548 | 1161 | 595 | 566 | 260 | 4.5 | - | NIL | 0.5 |  |  | 79
21.04.25 | 8.18 | 20 |  | NIL | 2307 | 1546 | 1119 | 595 | 524 | 236 | 4.5 | - | NIL | 0.5 |  |  | 72
22.04.25 | 6.59 | 16 |  | NIL | 1882 | 1261 | 1085 | 571 | 514 | 228 | 4.2 | - | NIL | 0.5 |  |  | 76
23.04.25 | 7.35 | 26 |  | 0.3 | 1719 | 1152 | 1066 | 585 | 481 | 236 | 4.3 | - | NIL | 0.6 |  |  | 79
24.04.25 | 7.06 | 20 |  | NIL | 1829 | 1226 | 1009 | 571 | 438 | 197 | 4.5 | - | NIL | 0.5 |  |  | 81
25.04.25 | 7.01 | 17 |  | NIL | 2240 | 1501 | 1042 | 581 | 461 | 213 | 4.2 | - | NIL | 0.5 |  |  | 76
26.04.25 | 7.59 | 18 |  | NIL | 1925 | 1290 | 1033 | 569 | 464 | 209 | 4.3 | - | NIL | 0.5 |  |  | 75
28.04.25 | 7.07 | 21 |  | NIL | 2083 | 1396 | 1028 | 585 | 443 | 181 | 4.4 | - | NIL | 0.5 |  |  | 79
29.04.25 | 7.52 | 21 |  | 0.6 | 2126 | 1425 | 1044 | 530 | 514 | 189 | 4.5 | - | NIL | 0.6 |  |  | 88
30.04.25 | 7.45 | 22 |  | 0.6 | 2579 | 1728 | 1142 | 510 | 632 | 158 | 4.3 | - | NIL | 0.5 |  |  | 83
01.05.25 | 7.19 | 23 |  | 0.5 | 3198 | 2143 | 1151 | 522 | 629 | 197 | 4.3 | - | - | 0.5 |  |  | 79
02.05.25 | 7.49 | 20 |  | 0.6 | 2303 | 1543 | 1142 | 612 | 530 | 189 | 4.2 | - | - | 0.6 |  |  | 74
03.05.25 | 7.4 | 20 |  | 0.6 | 2411 | 1616 | 1138 | 608 | 530 | 193 | 4.1 | - | - | 0.5 |  |  | 78
05.05.25 | 6.84 | 19 |  | 1 | 2395 | 1605 | 1187 | 628 | 559 | 197 | 4.4 | - | - | 0.5 |  |  | 79
06.05.25 | 7.05 | 17 |  | 0.5 | 2197 | 1472 | 1122 | 604 | 518 | 173 | 4.2 | - | - | 0.5 |  |  | 81
07.05.25 | 7.11 | 18 |  | 0.5 | 2098 | 1406 | 1134 | 616 | 518 | 181 | 4.3 | - | - | 0.5 |  |  | 83
08.05.25 | 7.19 | 21 |  | 0.5 | 2426 | 1626 | 998 | 531 | 467 | 189 | 4 | - | - | 0.5 |  |  | 88
09.05.25 | 7.12 | 26 |  | 0.8 | 2213 | 1483 | 990 | 535 | 455 | 181 | 4.2 | - | - | 0.4 |  |  | 80
10.05.25 | 7.68 | 20 |  | NIL | 2466 | 1652 | 994 | 531 | 463 | 173 | 4.1 | - | - | 0.5 |  |  | 85
12.05.25 | 7.01 | 18 |  | NIL | 2556 | 1713 | 978 | 519 | 459 | 181 | 4.1 | - | - | 0.5 |  |  | 78
13.05.25 | 7.7 | 24 |  | NIL | 2877 | 1928 | 986 | 507 | 479 | 173 | 4 | - | - | 0.5 |  |  | 78
14.05.25 | 7.74 | 23 |  | NIL | 2344 | 1571 | 998 | 535 | 463 | 189 | 4.3 | - | - | 0.6 |  |  | 87
15.05.25 | 7.5 | 20 |  | NIL | 2456 | 1646 | 990 | 581 | 409 | 181 | 4.5 | - | - | 0.5 |  |  | 79
16.05.25 | 7.61 | 20 |  | NIL | 2528 | 1694 | 994 | 523 | 471 | 157 | 4.2 | - | - | 0.5 |  |  | 82
17.05.25 | 7.23 | 15 |  | NIL | 3029 | 2030 | 981 | 519 | 462 | 161 | 4.3 | - | - | 0.5 |  |  | 80
19.05.25 | 7.19 | 20 |  | NIL | 2147 | 1439 | 972 | 510 | 462 | 165 | 4.2 | - | - | 0.5 |  |  | 82
20.05.25 | 7.14 | 22 |  | NIL | 2134 | 1430 | 986 | 506 | 480 | 181 | 4.1 | - | - | 0.5 |  |  | 86
21.05.25 | Shut Down
22.05.25 | Shut Down
23.05.25 | Shut Down
24.05.25 | Shut Down
26.05.25 | Shut Down
27.05.25 | Shut Down
28.05.25 | 7.85 | 23 |  | NIL | 559 | 375 | 220 | 180 | 40 | 150 | 4.1 | - | - | 0.5 |  |  | 82
29.05.25 | 7.4 | 22 |  | NIL | 789 | 529 | 211 | 176 | 35 | 151 | 4 | - | - | 0.5 |  |  | 79
30.05.25 | 7.41 | 23 |  | NIL | 1098 | 736 | 396 | 229 | 167 | 165 | 4.2 | - | - | 0.4 |  |  | 75
31.05.25 | 7.45 | 21 |  | NIL | 1141 | 765 | 392 | 224 | 168 | 151 | 4.1 | - | - | 0.4 |  |  | 78
02.06.25 | 6.86 | 22 |  | Nil | 1500 | 1005 | 409 | 220 | 189 | 165 | 4.3 | - | - | 0.4 |  |  | 80
03.06.25 | 6.98 | 22 |  | Nil | 1876 | 1257 | 415 | 227 | 188 | 173 | 4.2 | - | - | 0.5 |  |  | 78
04.06.25 | 7.15 | 20 |  | Nil | 1726 | 1157 | 544 | 248 | 296 | 180 | 4.3 | - | - | 0.6 |  |  | 88
05.06.25 | 6.76 | 20 |  | Nil | 2107 | 1412 | 551 | 253 | 298 | 187 | 4.5 | - | - | 0.4 |  |  | 86
06.06.25 | 7.15 | 18 |  | Nil | 2283 | 1530 | 564 | 260 | 304 | 173 | 4.8 | - | - | 0.4 |  |  | 89
07.06.25 | 6.86 | 20 |  | 0.5 | 2365 | 1585 | 556 | 246 | 310 | 180 | 4.4 | - | - | 0.5 |  |  | 82
09.06.25 | 7.5 | 18 |  | 0.5 | 2667 | 1787 | 519 | 244 | 275 | 186 | 4.8 | - | - | 0.5 |  |  | 81
10.06.25 | 7.15 | 25 |  | Nil | 2755 | 1846 | 515 | 229 | 286 | 178 | 4.2 | - | - | 0.5 |  |  | 75
11.06.25 | 7.46 | 23 |  | 0.5 | 2840 | 1903 | 584 | 248 | 336 | 200 | 4.3 | - | - | 0.6 |  |  | 76
12.06.25 | 7.1 | 11 | 7 | Nil | 2360 | 1581 | 840 | 520 | 320 | 354 | 6.3 | - | - | 0.2 |  |  | -
13.06.25 | 7.2 | 17 | 12 | Nil | 2330 | 1561 | 832 | 502 | 330 | 350 | 6.2 | - | - | 0.2 |  |  | -
14.06.25 | 7.6 | - | 10 | Nil | 2130 | 1427 | 809 | 488 | 321 | 342 | 6.1 | - | - | 0.2 |  |  | -
16.06.25 | 7.2 | - | 27 | 0.8 | 2260 | 1514 | 842 | 493 | 349 | 355 | 5.9 | 50 | - | 0.2 |  |  | -
17.06.25 | 7.2 | - | 26 | 0.4 | 2260 | 1510 | 780 | 486 | 294 | 280 | 6.1 | 35 | - | 0.2 |  |  | -
18.06.25 | 7.05 | - | 20 | Nil | 2586 | 1733 | 624 | 243 | 381 | 178 | 4.4 | - | - | 0.4 |  |  | 71
19.06.25 | 7.44 | - | 16 | 0.6 | 2488 | 1667 | 600 | 328 | 272 | 186 | 4.3 | - | - | 0.5 |  |  | 73
20.06.25 | 7.46 | - | 18 | Nil | 2425 | 1625 | 602 | 319 | 283 | 171 | 4.2 | - | - | 0.4 |  |  | 70
21.06.25 | 7.6 | - | 19 | Nil | 2541 | 1703 | 609 | 324 | 285 | 178 | 4.2 | - | - | 0.5 |  |  | 74
23.06.25 | 8.36 | - | 22 | Nil | 2326 | 1559 | 600 | 317 | 283 | 182 | 4.3 | - | - | 0.4 |  |  | 75
24.06.25 | 7.47 | - | 24 | Nil | 2611 | 1750 | 595 | 305 | 290 | 171 | 4.2 | - | - | 0.5 |  |  | 77
25.06.25 | 7.09 | - | 20 | 0.5 | 2623 | 1758 | 622 | 357 | 265 | 157 | 4.3 | - | - | 0.6 |  |  | 75
26.06.25 | 7.36 | - | 16 | Nil | 2600 | 1742 | 626 | 361 | 265 | 171 | 4.5 | - | - | 0.5 |  |  | 79
27.06.25 | 8.1 | - | 20 | Nil | 2713 | 1818 | 634 | 357 | 277 | 168 | 4.2 | - | - | 0.5 |  |  | 75
28.05.25 | 7.55 | - | 25 | Nil | 2425 | 1625 | 630 | 349 | 281 | 164 | 4 | - | - | 0.5 |  |  | 71
30.06.25 | 7.54 | - | 20 | Nil | 2432 | 1630 | 636 | 352 | 284 | 164 | 4.1 | - | - | 0.5 |  |  | 76
01.07.25 | 6.88 | - | 24 | Nil | 2611 | 1750 | 628 | 360 | 268 | 171 | 4.2 | - | - | 0.5 |  |  | 75
02.07.25 | 7.02 | - | 20 | Nil | 2628 | 1761 | 636 | 356 | 280 | 164 | 4.3 | - | - | 0.5 |  |  | 69
03.07.25 | 6.98 | - | 22 | Nil | 3104 | 2080 | 644 | 365 | 279 | 185 | 4.5 | - | - | 0.5 |  |  | 67
04.07.25 | 6.78 | - | 20 | Nil | 2820 | 1890 | 628 | 365 | 263 | 177 | 4.6 | - | - | 0.5 |  |  | 65
05.07.25 | 7.3 | - | 20 | Nil | 2716 | 1820 | 636 | 348 | 288 | 194 | 4.4 | - | - | 0.5 |  |  | 71
07.07.25 | 7.5 | - | 18 | Nil | 2502 | 1679 | 632 | 360 | 272 | 194 | 4.5 | - | - | 0.5 |  |  | 72
08.07.25 | 6.73 | - | 22 | 0.6 | 2723 | 1825 | 628 | 365 | 263 | 153 | 4.4 | - | - | 0.5 |  |  | 74
09.07.25 | 7.86 | - | 22 | 0.2 | 2208 | 1480 | 784 | 403 | 381 | 182 | 4.2 | - | - | 0.5 |  |  | 78
10.07.25 | 6.78 | - | 18 | Nil | 2522 | 1690 | 797 | 390 | 407 | 167 | 4.5 | - | - | 0.5 |  |  | 70
11.07.25 | 7.27 | - | 18 | Nil | 2823 | 1892 | 814 | 390 | 424 | 189 | 4.6 | - | - | 0.5 |  |  | 75
12.07.25 | 6.86 | - | 25 | Nil | 3164 | 2120 | 827 | 399 | 428 | 160 | 4.5 | - | - | 0.5 |  |  | 82
14.07.25 | 6.98 | - | 19 | Nil | 3119 | 2090 | 810 | 390 | 420 | 167 | 4.3 | - | - | 0.5 |  |  | 74
15.07.25 | 7.02 | - | 20 | Nil | 3179 | 2130 | 806 | 386 | 420 | 145 | 4.2 | - | - | 0.5 |  |  | 73
16.07.25 | 7.25 | - | 20 | Nil | 3097 | 1840 | 1039 | 551 | 488 | 204 | 4.1 | - | - | 0.4 |  |  | 81
17.07.25 | 7.75 | - | 17 | Nil | 2965 | 1987 | 1052 | 557 | 495 | 182 | 4.3 | - | - | 0.5 |  |  | 78
18.07.25 | 7.5 | - | 19 | Nil | 2425 | 1628 | 1036 | 583 | 453 | 189 | 4.2 | - | - | 0.5 |  |  | 72
19.07.25 | 6.75 | - | 20 | 0.1 | 1779 | 1192 | 1058 | 570 | 488 | 174 | 4.5 | - | - | 0.5 |  |  | 76
21.07.25 | 7.12 | - | 20 | Nil | 1818 | 1218 | 1076 | 572 | 504 | 178 | 4.5 | - | - | 0.5 |  |  | 76
22.07.25 | 6.85 | - | 21 | Nil | 1680 | 1126 | 1071 | 579 | 492 | 170 | 4.2 | - | - | 0.5 |  |  | 72
23.07.25 | 6.68 | - | 16 | Nil | 2435 | 1632 | 1058 | 583 | 475 | 163 | 4.3 | - | - | 0.6 |  |  | 70
24.07.25 | 7.3 | - | 22 | 0.5 | 1788 | 1198 | 1067 | 579 | 488 | 160 | 4.4 | - | - | 0.5 |  |  | 72
25.07.25 | 7.33 | - | 18 | Nil | 1658 | 1111 | 1076 | 570 | 506 | 178 | 4.5 | - | - | 0.5 |  |  | 75
26.07.25 | 7.63 | - | 20 | 0.1 | 2456 | 1646 | 1058 | 583 | 475 | 156 | 4.3 | - | - | 0.5 |  |  | 85
28.07.25 | 6.56 | - | 31 | 0.6 | 2923 | 1959 | 1061 | 581 | 480 | 163 | 4.4 | - | - | 0.5 |  |  | 79
29.07.25 | 6.95 | - | 55 | Nil | 2668 | 1788 | 1072 | 580 | 492 | 156 | 4.3 | - | - | 0.4 |  |  | 74
30.07.25 | 6.98 | - | 32 | Nil | 2685 | 1799 | 1104 | 511 | 593 | 150 | 4.5 | - | - | 0.6 |  |  | 75
31.07.25 | 7.48 | - | 25 | 0.6 | 2493 | 1670 | 1095 | 621 | 474 | 163 | 4.5 | - | - | 0.6 |  |  | 79
01.08.25 | 6.68 | - | 21 | Nil | 2562 | 1717 | 1066 | 628 | 438 | 170 | 4.3 | - | - | 0.5 |  |  | 81
02.08.25 | 6.76 | - | 22 | Nil | 2468 | 1654 | 1052 | 619 | 433 | 163 | 4.1 | - | - | 0.4 |  |  | 85
04.08.25 | 7.27 | - | 22 | Nil | 1747 | 1171 | 1054 | 619 | 435 | 144 | 4.1 | - | - | 0.5 |  |  | 78
05.08.25 | 6.62 | - | 22 | Nil | 2165 | 1451 | 1047 | 614 | 433 | 129 | 4.2 | - | - | 0.5 |  |  | 81
06.08.25 | 7.72 | - | 26 | Nil | 1841 | 1234 | 1052 | 624 | 428 | 195 | 4.1 | - | - | 0.5 |  |  | 86
07.08.25 | 7.7 | - | 21 | Nil | 1916 | 1284 | 1057 | 619 | 438 | 118 | 4.2 | - | - | - |  |  | 80
08.08.25 | 7.46 | - | 20 | 0.5 | 1999 | 1339 | 1066 | 614 | 452 | 144 | 4 | - | - | 0.4 |  |  | 85
11.08.25 | 7.73 | - | 20 | 0.1 | 1858 | 1245 | 1057 | 571 | 486 | 165 | 4.5 | - | - | 0.4 |  |  | 80
12.08.25 | 8.06 | - | 22 | Nil | 1680 | 1126 | 1061 | 576 | 485 | 158 | 4.4 | - | - | 0.5 |  |  | 77
13.08.25 | 8.04 | - | 21 | 0.1 | 1504 | 1008 | 857 | 614 | 243 | 151 | 4.2 | - | - | 0.4 |  |  | 78
14.08.25 | 7.16 | - | 22 | 1 | 1520 | 1019 | 838 | 600 | 238 | 165 | 4.1 | - | - | 0.5 |  |  | 72
15.08.25 | 8.39 | - | 18 | Nil | 1673 | 1121 | 852 | 595 | 257 | 151 | 4.2 | - | - | 0.5 |  |  | 70
18.08.25 | 8.83 | - | 22 | Nil | 1914 | 1283 | 837 | 581 | 256 | 149 | 4.2 | - | - | 0.4 |  |  | 78
19.08.25 | 7.6 | - | 19 | Nil | 2971 | 1991 | 914 | 585 | 329 | 142 | 4.1 | - | - | 0.5 |  |  | 72
20.08.25 | 8.49 | - | 18 | Nil | 2137 | 1432 | 909 | 576 | 333 | 156 | 4 | - | - | 0.5 |  |  | 74
21.08.25 | 8.02 | - | 21 | 0.5 | 2449 | 1641 | 928 | 571 | 357 | 156 | 4.3 | - | - | 0.5 |  |  | 76
22.08.25 | 8.22 | - | 18 | 0.2 | 1765 | 1183 | 923 | 574 | 349 | 142 | 4.4 | - | - | 0.5 |  |  | 79
23.08.25 | 8.14 | - | 20 | Nil | 1768 | 1185 | 628 | 581 | 47 | 163 | 4.5 | - | - | 0.5 |  |  | 81
25.08.25 | 8.5 | - | 19 | 0.4 | 2568 | 1721 | 919 | 571 | 348 | 149 | 4.3 | - | - | 0.5 |  |  | 74
26.08.25 | 8.53 | - | 18 | 0.5 | 2755 | 1846 | 927 | 578 | 349 | 142 | 4 | - | - | 0.5 |  |  | 76
27.08.25 | 7.85 | - | 20 | 0.5 | 2559 | 1715 | 1008 | 627 | 381 | 163 | 4.2 | - | - | 0.5 |  |  | 80
28.08.25 | 8.44 | - | 18 | 0.6 | 2676 | 1793 | 1035 | 650 | 385 | 156 | 4.4 | - | - | 0.6 |  |  | 76
29.08.25 | 8.32 | - | 24 | Nil | 2741 | 1837 | 1024 | 641 | 383 | 149 | 4.3 | - | - | 0.5 |  |  | 79
| 0.5 | 17 |  | 0.1 | 559 | 375 | 211 | 176 | 35 | 142 | 5.8 | 35 | 0 | 0.2 | 0 | 0 | 36
MAX. | 8.83 | 28 |  | 1 | 3731 | 2500 | 1498 | 795 | 869 | 483 | 10.5 | 50 | 0 | 0.9 | 0 | 0 | 95
AVG. | 7.3491 | 19 |  | 0.57021 | 2440.5597 | 1636.5643 | 930.5925 | 510.7335 | 420.0313 | 268.125 | 3.8828 | 42.5 | 0 | 0.50317 |  |  | 79.3854
No. of < Spec | 206 | -- |  | 12 | -- | -- | -- | -- | -- | -- | 315 | -- | -- | -- | -- | -- | --
No. of > Spec | 21 | 189 |  | 69 | -- | 23 | 36 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 64.5768 | -- |  | 8.5106 | -- | -- | -- | -- | -- | -- | 98.7461 | [5 empty] | --
% > Specs. | 6.5831 | 74.1176 |  | 48.9362 |  | 7.21 | 11.2853 |  | -- | 0 | 0 | 0 |  | 0 |  |  | 0