## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | Sulphate | SiO2 | IRON
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm | 3.0 ppm
01.08.16 | 7.4 | 68 | 0.1 | 1360 | 903 | 584 | 319 | 210 | 7 | 10 | 110 | - | 154 | 0.9
02.08.16 | 7.38 | 70 | 0.4 | 1370 | 916 | 542 | 374 | 218 | 7 | 10 | 120 | - | 148 | 0.9
03.08.16 | 7.34 | 66 | 0.1 | 1204 | 840 | 584 | 256 | 202 | 7.1 | 10.1 | 115 | - | 142 | 0.9
04.08.16 | 7.42 | 78 | 0 | 1279 | 869 | 538 | 331 | 210 | 7.2 | 10.2 | 110 | - | 148 | 0.9
05.08.16 | 7.48 | 69 | 0 | 1170 | 765 | 470 | 295 | 208 | 7.2 | 10.2 | 115 | - | 146 | 0.9
06.08.16 | 7.5 | 65 | 0 | 1056 | 722 | 466 | 256 | 195 | 7.2 | 10.2 | 112 | - | 152 | 0.9
07.08.16 | 7.57 | 78 | 0 | 1182 | 735 | 480 | 255 | 196 | 7.1 | 10.1 | 115 | - | 158 | 1
08.08.16 | 7.65 | 83 | 0 | 1286 | 742 | 488 | 254 | 195 | 7.1 | 10.2 | 110 | - | 156 | 1.2
09.08.16 | 7.98 | 70 | 0 | 1295 | 722 | 475 | 247 | 187 | 7.3 | 10.3 | 109 | - | 162 | 0.9
10.08.16 | 7.9 | 66 | 0 | 1153 | 672 | 433 | 239 | 171 | 7.2 | 10.2 | 120 | - | 160 | 0.8
11.08.16 | 8.06 | 54 | 0 | 930 | 622 | 437 | 185 | 179 | 7.2 | 10.2 | 115 | - | 160 | 0.9
12.08.16 | 8.01 | 60 | 0 | 922 | 615 | 430 | 185 | 172 | 7.2 | 10.2 | 115 | - | 160 | 0.8
13.08.16 | 8.2 | 49 | 0 | 901 | 554 | 374 | 180 | 179 | 7.1 | 10.1 | 120 | - | 158 | 0.8
14.08.16 | 8 | 55 | 0 | 880 | 548 | 370 | 178 | 176 | 7.2 | 10.2 | 118 | - | 158 | 0.8
15.08.16 | 7.98 | 58 | 0 | 790 | 530 | 355 | 175 | 170 | 7.2 | 10.2 | 115 | - | 158 | 0.8
16.08.16 | 7.9 | 63 | 0 | 724 | 500 | 315 | 185 | 159 | 7.4 | 10.4 | 110 | - | 159 | 0.8
17.08.16 | 7.7 | 77 | 0 | 808 | 466 | 319 | 147 | 162 | 7.5 | 10.5 | 110 | - | 160 | 0.9
18.08.16 | 7.62 | 80 | 0 | 820 | 488 | 352 | 168 | 158 | 7.1 | 10.1 | 110 | - | 161 | 1.9
19.08.16 | 7.82 | 83 | 0 | 853 | 520 | 352 | 168 | 158 | 7.1 | 10.1 | 110 | - | 161 | 1.9
20.08.16 | 7.32 | 81 | 0 | 820 | 491 | 332 | 159 | 156 | 7.1 | 10.1 | 110 | - | 158 | 1.9
21.08.16 | 7.22 | 81 | 0 | 780 | 470 | 310 | 160 | 158 | 7.1 | 10.1 | 110 | - | 158 | 1.9
22.08.16 | 7.32 | 88 | 0 | 880 | 545 | 370 | 175 | 160 | 7.1 | 10.1 | 110 | - | 160 | 1.9
23.08.16 | 7.46 | 97 | 0 | 827 | 525 | 361 | 164 | 162 | 7.2 | 10.2 | 113 | - | 163 | 1.9
24.08.16 | 7.48 | 99 | 0 | 682 | 496 | 260 | 236 | 156 | 7.3 | 10.3 | 110 | - | 162 | 1.8
25.08.16 | 7.46 | 100 | 0 | 685 | 498 | 269 | 229 | 152 | 7.4 | 10.4 | 102 | - | 161 | 1.9
26.08.16 | 7.1 | 104 | 0 | 510 | 480 | 256 | 224 | 154 | 7.3 | 10.33 | 110 | - | 163 | 1.8
27.08.16 | 6.94 | 112 | 0 | 535 | 504 | 315 | 189 | 181 | 7.5 | 10.5 | 109 | - | 159 | 1.9
28.08.16 | 7.44 | 110 | 0 | 788 | 502 | 309 | 193 | 180 | 7.4 | 10.4 | 100 | - | 162 | 2.2
29.08.16 | 7.44 | 110 | 0 | 788 | 498 | 302 | 196 | 180 | 7.4 | 10.4 | 100 | - | 162 | 2.2
30.08.16 | 7.42 | 118 | 0 | 735 | 470 | 315 | 155 | 173 | 7.8 | 10.8 | 110 | - | 166 | 2.6
31.08.16 | 7.84 | 103 | 0 | 949 | 483 | 298 | 185 | 173 | 7.9 | 10.9 | 110 | - | 163 | 2.8
MIN. | 6.94 | 49 | 0 | 510 | 466 | 256 | 147 | 152 | 7 | 10 | 100 | 0 | 142 | 0.8
MAX. | 8.2 | 118 | 0.4 | 1370 | 916 | 584 | 374 | 218 | 7.9 | 10.9 | 120 | 0 | 166 | 2.8
AVG. | 7.5919 | 80.4839 | 0 | 934.2581 | 602.9355 | 389.0645 | 214.9032 | 177.0968 | 0 | 10.259 | 111.3871 | 0 | 0 | 1.4097
No. of < Spec | 16 | -- | 30 | -- | -- |  | -- | -- | 0 | 0 | 0 | -- | -- | 31
No. of > Spec | 3 | 31 | 0 | 0 | 0 | -- | -- | 0 | 0 | 31 | 31 | 0 | 0 | 0
% < Specs. | 51.6129 | -- | 96.7742 | -- | -- | -- | -- | -- | 0 | 0 | 0 | - | -- | 100
% > Specs. | 9.6774 | 100 | 0 | 0 | 0 | - | -- | 0 | 0 | 100 | 100 |  | 0 | 0