## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-06-01 | 7.64 | 23 | 0.1 | 978 | 260 | 156 | 104 | 241 | 6.9 | 10.9 | 102 | 580 | 89
2017-06-02 | 7.6 | 25 | 0.2 | 983 | 264 | 160 | 104 | 249 | 6.9 | 10.9 | 100 | 573 | 87
2017-06-03 | 8 | 24 | 0.1 | 959 | 268 | 164 | 104 | 256 | 6.6 | 10.6 | 104 | 570 | 85
2017-06-04 | 8 | 23 | 0.2 | 952 | 256 | 154 | 102 | 258 | 6.6 | 106 | 102 | 575 | 88
2017-06-05 | 7.9 | 22 | 0.2 | 940 | 252 | 152 | 100 | 260 | 6.5 | 10.5 | 100 | 579 | 90
2017-06-06 | 7.68 | 16 | 0.2 | 953 | 260 | 156 | 104 | 249 | 6.7 | 10.37 | 100 | 562 | 82
2017-06-07 | 7.75 | 16 | 0.2 | 920 | 252 | 144 | 108 | 241 | 6.9 | 10.9 | 100 | 572 | 89
2017-06-08 | 7.72 | 16 | 0.2 | 957 | 256 | 148 | 108 | 249 | 7 | 11 | 102 | 579 | 90
2017-06-09 | 7.7 | 21 | 0.1 | 968 | 260 | 148 | 112 | 241 | 7.2 | 11.2 | 103 | 570 | 92
2017-06-10 | 7.94 | 17 | 0.1 | 948 | 256 | 144 | 112 | 234 | 7 | 11 | 100 | 582 | 87
2017-06-11 | 7.82 | 18 | 0.1 | 998 | 254 | 142 | 112 | 265 | 6.9 | 10.9 | 102 | 586 | 85
2017-06-12 | 7.54 | 19 | 0.2 | 1052 | 252 | 140 | 112 | 271 | 7 | 11 | 100 | 589 | 83
2017-06-13 | 7.39 | 49 | 0.2 | 2250 | 272 | 160 | 112 | 840 | 7.5 | 11.5 | 98 | 593 | 98
2017-06-14 | 7.68 | 47 | 0.1 | 2980 | 260 | 144 | 116 | 840 | 7.6 | 11.6 | 102 | 640 | 110
2017-06-15 | 7.72 | 50 | 0.1 | 2840 | 248 | 149 | 99 | 842 | 7.5 | 11.5 | 100 | 652 | 112
2017-06-16 | 7.1 | 48 | 0.2 | 2390 | 252 | 152 | 100 | 753 | 7 | 11 | 100 | 666 | 115
2017-06-17 | 7.29 | 46 | 0.2 | 2310 | 250 | 149 | 101 | 790 | 7.2 | 11.2 | 100 | 670 | 112
2017-06-18 | 7.4 | 38 | 0.1 | 1950 | 252 | 152 | 100 | 665 | 7.1 | 11.1 | 102 | 678 | 112
2017-06-19 | 7.49 | 34 | 0.1 | 1680 | 256 | 156 | 100 | 527 | 6.9 | 10.9 | 100 | 689 | 110
2017-06-20 | 8.09 | 16 | 0.1 | 1240 | 249 | 148 | 101 | 475 | 7 | 11 | 105 | 694 | 125
2017-06-21 | 7.56 | 15 | 0.1 | 1120 | 260 | 150 | 110 | 351 | 7.2 | 11.2 | 102 | 690 | 120
2017-06-22 | 7.9 | 17 | 0.1 | 1045 | 264 | 160 | 104 | 307 | 7 | 11 | 100 | 682 | 115
2017-06-23 | 7.38 | 20 | 0.1 | 985 | 248 | 152 | 96 | 293 | 7 | 11 | 102 | 589 | 110
2017-06-24 | 8.2 | 20 | 0.2 | 1026 | 240 | 140 | 100 | 300 | 7.3 | 11.3 | 106 | 576 | 109
2017-06-25 | 8.1 | 19 | 0.1 | 1085 | 242 | 142 | 100 | 295 | 7.2 | 11.2 | 105 | 572 | 105
2017-06-26 | 7.52 | 18 | 0.1 | 1105 | 244 | 144 | 100 | 285 | 7.2 | 11.2 | 104 | 570 | 102
2017-06-27 | 7.47 | 14 | 0.2 | 940 | 252 | 152 | 100 | 271 | 7 | 11 | 103 | 550 | 98
2017-06-28 | 7.73 | 20 | 0.1 | 974 | 256 | 152 | 104 | 256 | 6.8 | 10.8 | 100 | 552 | 95
2017-06-29 | 8.18 | 25 | 0.1 | 993 | 247 | 148 | 99 | 263 | 7 | 11 | 100 | 533 | 98
2017-06-30 | 7.95 | 20 | 0.3 | 958 | 251 | 148 | 103 | 256 | 7.2 | 11.2 | 105 | 530 | 92
MIN. | 7.1 | 14 | 0.1 | 920 | 240 | 140 | 96 | 234 | 6.5 | 10.37 | 98 | 530 | 82
MAX. | 8.2 | 50 | 0.3 | 2980 | 272 | 164 | 116 | 842 | 7.6 | 106 | 106 | 694 | 125
AVG. | 7.7147 | 25.2 | 0.14667 | 1315.9667 | 254.4333 | 150.2 | 104.2414 | 387.4333 | 7.03 | 14.199 | 101.6333 | 601.4333 | 99.5
No. of < Spec | 7 | -- | 16 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 3 | 13 | 0 | 5 | 0 | -- | -- | 7 | 0 | 0 | - | 0 | 0
% < Specs. | 25 | -- | 57.1429 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 10.7143 | 46.4286 | 0 | 17.8571 | 0 | - | -- | 25 | 0 | 0 | - | 0 | 0