## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-03-01 | 7.38 | 18 | 0.1 | 1457 | 604 | 355 | 249 | 252 | 6.9 | 10.9 | 103 | 653 | 125
2018-03-02 | 7.48 | 17 | 0.1 | 1480 | 630 | 372 | 258 | 262 | 6.8 | 10.8 | 102 | 652 | 132
2018-03-03 | 7.5 | 16 | 0.2 | 1520 | 673 | 384 | 289 | 274 | 6.9 | 10.9 | 100 | 643 | 140
2018-03-04 | 7.6 | 20 | 0.1 | 1550 | 680 | 390 | 290 | 268 | 7 | 11 | 100 | 652 | 142
2018-03-05 | 7.5 | 24 | 0.1 | 1530 | 650 | 359 | 291 | 265 | 7.2 | 11.2 | 102 | 660 | 139
2018-03-06 | 7.62 | 22 | 0.1 | 1470 | 661 | 367 | 294 | 267 | 6.7 | 10.7 | 103 | 643 | 146
2018-03-07 | 7.6 | 25 | 0.1 | 1340 | 653 | 363 | 290 | 259 | 7 | 11 | 102 | 658 | 133
2018-03-08 | 7.48 | 20 | 0.1 | 1170 | 645 | 355 | 290 | 252 | 6.9 | 10.9 | 107 | 652 | 120
2018-03-09 | 7.38 | 17 | 0.1 | 1228 | 653 | 363 | 290 | 267 | 6.9 | 10.9 | 103 | 650 | 115
2018-03-10 | 7.76 | 18 | 0.1 | 1220 | 649 | 359 | 290 | 259 | 6.9 | 10.9 | 100 | 630 | 139
2018-03-11 | 7.74 | 17 | 0.1 | 1250 | 630 | 345 | 285 | 238 | 6.8 | 10.8 | 102 | 645 | 135
2018-03-12 | 7.7 | 17 | 0.1 | 1270 | 604 | 355 | 249 | 231 | 6.7 | 10.7 | 100 | 670 | 132
2018-03-13 | 7.33 | 19 | 0.1 | 1250 | 608 | 363 | 245 | 238 | 6.7 | 10.7 | 98 | 660 | 128
2018-03-14 | 7.52 | 15 | 0.1 | 1340 | 571 | 335 | 236 | 231 | 6.7 | 10.7 | 100 | 653 | 132
2018-03-15 | 7.78 | 17 | 0.1 | 1420 | 604 | 355 | 249 | 259 | 6.8 | 10.8 | 100 | 658 | 136
2018-03-16 | 7.59 | 16 | 0.1 | 1372 | 616 | 343 | 273 | 274 | 6.7 | 10.7 | 105 | 689 | 127
2018-03-17 | 7.53 | 16 | 0.1 | 1390 | 588 | 326 | 262 | 267 | 6.9 | 10.9 | 105 | 673 | 132
2018-03-18 | 7.62 | 17 | 0.1 | 1540 | 610 | 340 | 270 | 280 | 6.8 | 10.8 | 104 | 670 | 128
2018-03-19 | 7.72 | 17 | 0.1 | 1688 | 680 | 369 | 311 | 310 | 6.8 | 10.8 | 100 | 669 | 130
2018-03-20 | 7.68 | 18 | 0.1 | 1702 | 661 | 355 | 306 | 303 | 6.5 | 10.5 | 109 | 680 | 138
2018-03-21 | 7.7 | 18 | 0.1 | 1620 | 653 | 347 | 306 | 295 | 6.9 | 10.9 | 116 | 693 | 125
2018-03-22 | 7.68 | 14 | 0.1 | 1502 | 632 | 332 | 300 | 288 | 6.5 | 10.5 | 117 | 640 | 120
2018-03-23 | 7.65 | 14 | 0.1 | 1683 | 652 | 356 | 296 | 303 | 6.7 | 10.7 | 114 | 653 | 129
2018-03-24 | 7.83 | 14 | 0.1 | 1670 | 648 | 352 | 296 | 295 | 6.6 | 10.6 | 110 | 655 | 122
2018-03-25 | 7.88 | 14 | 0.1 | 1676 | 650 | 354 | 294 | 292 | 6.7 | 10.7 | 112 | 648 | 124
2018-03-26 | 7.9 | 15 | 0.1 | 1680 | 640 | 350 | 290 | 290 | 6.7 | 10.7 | 113 | 640 | 120
2018-03-27 | 7.2 | 17 | 0.1 | 1539 | 604 | 332 | 272 | 295 | 6.5 | 10.5 | 115 | 633 | 122
2018-03-28 | 7.67 | 16 | 0.1 | 1530 | 628 | 352 | 276 | 310 | 6.7 | 10.7 | 105 | 648 | 120
2018-03-29 | 7.68 | 17 | 0.1 | 1560 | 620 | 343 | 277 | 312 | 6.8 | 10.8 | 110 | 630 | 125
2018-03-30 | 7.72 | 18 | 0.1 | 1410 | 540 | 330 | 210 | 240 | 6.8 | 10.8 | 112 | 650 | 120
2018-03-31 | 7.6 | 18 | 0.1 | 1250 | 508 | 333 | 175 | 214 | 6.7 | 10.7 | 114 | 630 | 118
MIN. | 7.2 | 14 | 0.1 | 1170 | 508 | 326 | 175 | 214 | 6.5 | 10.5 | 98 | 630 | 115
MAX. | 7.9 | 25 | 0.2 | 1702 | 680 | 390 | 311 | 312 | 7.2 | 11.2 | 117 | 693 | 146
AVG. | 7.6135 | 17.4516 | 0.10323 | 1461.5161 | 627.2581 | 352.7097 | 275.3333 | 270.6452 | 6.7806 | 10.7806 | 105.9032 | 654.1935 | 128.8387
No. of < Spec | 6 | -- | 27 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 3 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 21.4286 | -- | 96.4286 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 10.7143 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0