## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.5 - 8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2017-12-01 | 7.02 | 16 | 0.1 | 1840 | 1119 | 610 | 509 | 267 | 4 | 106 | 0.2 | 910 | 189
2017-12-02 | 7.39 | 19 | 0.2 | 1887 | 1110 | 610 | 500 | 274 | 4 | 103 | 0.2 | 884 | 182
2017-12-03 | 7.3 | 18 | 0.3 | 1840 | 1095 | 590 | 505 | 272 | 4 | 102 | 0.2 | 890 | 178
2017-12-04 | 7.53 | 18 | 0.2 | 1980 | 1070 | 580 | 490 | 275 | 4.1 | 100 | 0.2 | 879 | 170
2017-12-05 | 7.42 | 16 | 0.1 | 2094 | 1081 | 583 | 498 | 281 | 4 | 103 | 0.2 | 830 | 172
2017-12-06 | 7.46 | 17 | 0.2 | 1990 | 1220 | 661 | 559 | 303 | 4 | 100 | 0.2 | 834 | 179
2017-12-07 | 7.7 | 16 | 0.2 | 2010 | 1223 | 663 | 560 | 295 | 4.2 | 104 | 0.2 | 870 | 189
2017-12-08 | 7.73 | 17 | 0.2 | 2018 | 1187 | 619 | 568 | 288 | 4 | 102 | 0.2 | 853 | 192
2017-12-09 | 7.4 | 18 | 0.2 | 1940 | 1193 | 619 | 574 | 289 | 4 | 100 | 0.2 | 878 | 196
2017-12-10 | 7.29 | 19 | 0.2 | 1967 | 1210 | 628 | 582 | 290 | 4 | 102 | 0.2 | 880 | 194
2017-12-11 | 7.42 | 16 | 0.2 | 1994 | 1219 | 640 | 579 | 300 | 4 | 102 | 0.2 | 883 | 198
2017-12-12 | 7.49 | 17 | 0.2 | 2029 | 1354 | 743 | 611 | 318 | 4.1 | 104 | 0.3 | 910 | 200
2017-12-13 | 7.3 | 16 | 0.2 | 1962 | 1318 | 694 | 624 | 321 | 4 | 102 | 0.3 | 842 | 195
2017-12-14 | 7.63 | 15 | 0.2 | 1893 | 1322 | 743 | 579 | 328 | 4 | 104 | 0.2 | 850 | 198
2017-12-15 | 7.16 | 17 | 0.3 | 1973 | 1334 | 722 | 612 | 335 | 4 | 100 | 0.2 | 897 | 190
2017-12-16 | 7.32 | 17 | 0.5 | 1932 | 1340 | 729 | 611 | 321 | 4 | 103 | 0.2 | 910 | 187
2017-12-17 | 7.2 | 18 | 0.2 | 2073 | 1390 | 752 | 638 | 324 | 4 | 100 | 0.2 | 924 | 201
2017-12-18 | 7.32 | 17 | 0.2 | 2090 | 1410 | 790 | 620 | 325 | 4 | 102 | 0.2 | 920 | 200
2017-12-19 | 7.25 | 17 | 0.1 | 2110 | 1424 | 755 | 669 | 328 | 4 | 100 | 0.2 | 942 | 203
2017-12-20 | 7.29 | 16 | 0.1 | 2153 | 1387 | 732 | 655 | 331 | 4 | 103 | 0.3 | 912 | 207
2017-12-21 | 7.12 | 19 | 0.1 | 2143 | 1410 | 689 | 721 | 337 | 4 | 100 | 0.3 | 930 | 210
2017-12-22 | 7.18 | 15 | 0.1 | 2260 | 1457 | 747 | 710 | 364 | 4 | 100 | 0.3 | 954 | 218
2017-12-23 | 7.18 | 16 | 0.1 | 2140 | 1416 | 734 | 682 | 357 | 4 | 103 | 0.3 | 980 | 220
2017-12-24 | 7.09 | 17 | 0.1 | 2180 | 1430 | 748 | 682 | 359 | 4 | 104 | 0.3 | 978 | 222
2017-12-25 | 7.1 | 18 | 0.1 | 2330 | 1542 | 845 | 697 | 364 | 4 | 107 | 0.3 | 983 | 226
2017-12-26 | 7.42 | 18 | 0.1 | 2410 | 1663 | 882 | 781 | 392 | 4 | 100 | 0.3 | 993 | 229
2017-12-27 | 7.12 | 18 | 0.1 | 2450 | 1630 | 840 | 790 | 400 | 4 | 100 | 0.3 | 990 | 220
2017-12-28 | 7.12 | 15 | 0.1 | 2464 | 1758 | 942 | 816 | 400 | 4 | 103 | 0.3 | 985 | 239
2017-12-29 | 7.6 | 16 | 0.1 | 2443 | 1643 | 874 | 769 | 378 | 4 | 102 | 0.3 | 984 | 224
2017-12-30 | 7.52 | 17 | 0.1 | 2450 | 1653 | 890 | 763 | 372 | 4 | 103 | 0.3 | 989 | 228
2017-12-31 | 7.42 | 16 | 0.1 | 2469 | 1669 | 893 | 776 | 370 | 4 | 104 | 0.3 | 990 | 226
MIN. | 7.02 | 15 | 0.1 | 1840 | 1070 | 580 | 490 | 267 | 4 | 100 | 0.2 | 830 | 170
MAX. | 7.73 | 19 | 0.5 | 2469 | 1758 | 942 | 816 | 400 | 4.2 | 107 | 0.3 | 993 | 239
AVG. | 7.3384 | 16.9355 | 0.16774 | 2113.3548 | 1363.7742 | 727.3226 | 636.4516 | 327.6774 | 4.0129 | 102.1935 | 0.24516 | 917.871 | 202.6452
No. of < Spec | 25 | -- | 15 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 0 | 13 | 31 | 18 | -- | 0 | 0 | 0 | 0 |  | 27
% < Specs. | 80.6452 | -- | 48.3871 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 0 | 41.9355 | 100 | 0 | -- | 0 | 0 | 0 | 0 | 0 | 87.0968