## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.2-8.2 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2018-04-01 | 7.7 | 14 | 0.1 | 1568 | 950 | 528 | 422 | 248 | 4 | 116 | 0.2 | 973 | 190
2018-04-02 | 7.78 | 15 | 0.1 | 1543 | 936 | 516 | 420 | 245 | 4 | 116 | 0.2 | 970 | 188
2018-04-03 | 7.62 | 17 | 0.1 | 1539 | 922 | 498 | 424 | 296 | 4.1 | 120 | 0.2 | 962 | 176
2018-04-04 | 7.44 | 17 | 0.1 | 1630 | 928 | 512 | 416 | 267 | 4 | 118 | 0.2 | 954 | 162
2018-04-05 | 7.6 | 15 | 0.1 | 1622 | 922 | 492 | 430 | 273 | 4 | 120 | 0.2 | 964 | 158
2018-04-06 | 7.48 | 14 | 0.1 | 1633 | 952 | 516 | 436 | 281 | 4 | 112 | 0.2 | 952 | 155
2018-04-07 | 7.3 | 16 | 0.1 | 1654 | 980 | 516 | 464 | 231 | 4 | 110 | 0.2 | 960 | 152
2018-04-08 | 7.5 | 15 | 0.1 | 1585 | 963 | 504 | 459 | 232 | 4 | 110 | 0.2 | 958 | 150
2018-04-09 | 7.3 | 14 | 0.1 | 1749 | 1070 | 577 | 493 | 288 | 4 | 117 | 0.2 | 989 | 158
2018-04-10 | 7.68 | 16 | 0.1 | 1643 | 1036 | 553 | 483 | 282 | 4 | 113 | 0.2 | 993 | 153
2018-04-11 | 7.29 | 15 | 0.1 | 1640 | 1012 | 543 | 469 | 282 | 4 | 114 | 0.2 | 980 | 152
2018-04-12 | 7.4 | 14 | 0.1 | 1789 | 1259 | 690 | 569 | 282 | 4 | 112 | 0.2 | 1006 | 159
2018-04-13 | 7.38 | 14 | 0.1 | 1715 | 1065 | 545 | 520 | 304 | 4 | 116 | 0.2 | 1002 | 162
2018-04-14 | 7.22 | 14 | 0.1 | 1743 | 1048 | 562 | 486 | 320 | 4 | 119 | 0.2 | 1024 | 157
2018-04-15 | 7.39 | 14 | 0.1 | 1682 | 1036 | 557 | 479 | 290 | 4 | 100 | 0.2 | 984 | 156
2018-04-16 | 7.3 | 13 | 0.1 | 1670 | 1020 | 550 | 470 | 292 | 4 | 102 | 0.2 | 988 | 154
2018-04-17 | 7.58 | 14 | 0.1 | 1620 | 982 | 512 | 470 | 284 | 4 | 118 | 0.2 | 992 | 152
2018-04-18 | 7.38 | 13 | 0.1 | 1618 | 960 | 496 | 464 | 282 | 4 | 120 | 0.2 | 997 | 150
2018-04-19 | 7.46 | 14 | 0.1 | 1533 | 890 | 483 | 407 | 232 | 4 | 113 | 0.2 | 966 | 145
2018-04-20 | 7.53 | 15 | 0.1 | 1510 | 878 | 480 | 398 | 232 | 4 | 118 | 0.2 | 968 | 144
2018-04-21 | 7.33 | 15 | 0.1 | 1502 | 894 | 491 | 403 | 248 | 4 | 110 | 0.2 | 973 | 146
2018-04-22 | 7.23 | 15 | 0.1 | 1498 | 887 | 485 | 402 | 252 | 4 | 112 | 0.2 | 972 | 145
2018-04-23 | 7.33 | 15 | 0.1 | 1630 | 928 | 495 | 433 | 246 | 4 | 110 | 0.2 | 986 | 150
2018-04-24 | 7.4 | 15 | 0.1 | 1664 | 950 | 502 | 448 | 229 | 4 | 119 | 0.2 | 980 | 146
2018-04-25 | 7.5 | 15 | 0.1 | 1689 | 970 | 515 | 455 | 228 | 4 | 120 | 0.2 | 994 | 149
2018-04-26 | 7.44 | 17 | 0.1 | 1648 | 990 | 518 | 472 | 234 | 4 | 118 | 0.2 | 997 | 156
2018-04-27 | 7.23 | 18 | 0.1 | 1670 | 986 | 524 | 462 | 252 | 4 | 118 | 0.2 | 978 | 159
2018-04-28 | 7.4 | 17 | 0.1 | 1652 | 975 | 530 | 445 | 248 | 4 | 115 | 0.2 | 998 | 158
2018-04-29 | 7.5 | 13 | 0.1 | 1633 | 970 | 533 | 437 | 240 | 4 | 112 | 0.2 | 984 | 158
2018-04-30 | 7.87 | 15 | 0.1 | 1610 | 962 | 530 | 432 | 242 | 4 | 112 | 0.2 | 982 | 159
MIN. | 7.22 | 13 | 0.1 | 1498 | 878 | 480 | 398 | 228 | 4 | 100 | 0.2 | 952 | 144
MAX. | 7.87 | 18 | 0.1 | 1789 | 1259 | 690 | 569 | 320 | 4.1 | 120 | 0.2 | 1024 | 190
AVG. | 7.452 | 14.9333 | 0.1 | 1629.4 | 977.3667 | 525.1 | 453.3103 | 262.0667 | 4.0033 | 114.3333 | 0.2 | 980.8667 | 156.6333
No. of < Spec | 0 | -- | 30 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 0 | 0 | 8 | 0 | -- | 0 | 0 | 0 | 0 | 3 | 2
% < Specs. | 0 | -- | 100 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 0 | 0 | 26.6667 |  | -- | 0 | 0 | 0 | 0 | 10 | 6.6667
No. of < Spec | 22 | -- | 30 | -- | -- | -- | -- | -- | 1 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 1 | 0 | 9 | 0 | -- | 0 | 0 | 0 | 0 | 30 | 1
% < Specs. | 70.9677 | -- | 96.7742 | -- | -- | -- | -- | -- | 3.2258 | - | - | - | --
% > Specs. | 0 | 0 | 3.2258 | 0 | 30 | 0 | -- | 0 | 0 | 0 | 0 | 100 | 3.3333