## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.2-8.2 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2018-04-12 | 8 | 12 | 0.1 | 482 | 240 | 145 | 95 | 80 | 3 | 120 | 0.1 | - | 58
2018-04-13 | 8.07 | 14 | 0.1 | 473 | 279 | 154 | 125 | 58 | 3.5 | 122 | 0.1 | - | 49
2018-04-14 | 8.05 | 18 | 0.1 | 568 | 312 | 174 | 138 | 87 | 3.4 | 126 | 0.1 | - | 52
2018-04-15 | 8.12 | 14 | 0.1 | 846 | 354 | 196 | 158 | 123 | 3.5 | 129 | 0.1 | - | 68
2018-04-16 | 8.1 | 15 | 0.1 | 860 | 369 | 208 | 161 | 124 | 3.6 | 124 | 0.1 | 229 | 68
2018-04-17 | 8.1 | 16 | 0.1 | 890 | 373 | 210 | 163 | 130 | 3.6 | 122 | 0.1 | 296 | 72
2018-04-18 | 7.82 | 17 | 0.1 | 993 | 512 | 280 | 232 | 138 | 3.7 | 120 | 0.1 | 299 | 93
2018-04-19 | 7.94 | 23 | 0.1 | 1110 | 661 | 362 | 299 | 152 | 3.6 | 120 | 0.1 | 290 | 79
2018-04-20 | 7.79 | 21 | 0.1 | 1168 | 699 | 383 | 316 | 174 | 3.8 | 126 | 0.1 | 311 | 87
2018-04-21 | 7.89 | 21 | 0.1 | 1184 | 866 | 474 | 392 | 181 | 3.9 | 120 | 0.1 | 319 | 96
2018-04-22 | 7.9 | 19 | 0.1 | 1193 | 879 | 380 | 499 | 181 | 3.9 | 120 | 0.1 | 320 | 96
2018-04-23 | 7.88 | 22 | 0.1 | 1252 | 753 | 383 | 370 | 188 | 4 | 108 | 0.1 | 373 | 93
2018-04-24 | 7.6 | 21 | 0.1 | 1283 | 772 | 430 | 342 | 182 | 3.6 | 113 | 0.1 | 390 | 90
2018-04-25 | 7.84 | 21 | 0.1 | 1368 | 768 | 418 | 350 | 176 | 3.8 | 122 | 0.1 | 382 | 96
2018-04-26 | 7.72 | 20 | 0.1 | 1320 | 790 | 419 | 371 | 203 | 3.9 | 120 | 0.1 | 382 | 98
2018-04-27 | 7.76 | 16 | 0.1 | 1347 | 811 | 428 | 383 | 215 | 3.9 | 120 | 0.1 | 412 | 102
2018-04-28 | 7.86 | 18 | 0.1 | 1352 | 844 | 483 | 361 | 192 | 4 | 122 | 0.1 | 414 | 128
2018-04-29 | 7.59 | 17 | 0.1 | 1435 | 872 | 468 | 404 | 194 | 4 | 120 | 0.1 | 416 | 150
2018-04-30 | 7.64 | 16 | 0.1 | 1460 | 860 | 459 | 401 | 204 | 4 | 112 | 0.1 | 470 | 152
MIN. | 7.59 | 12 | 0.1 | 473 | 240 | 145 | 95 | 58 | 3 | 108 | 0.1 | 229 | 49
MAX. | 8.12 | 23 | 0.1 | 1460 | 879 | 483 | 499 | 215 | 4 | 129 | 0.1 | 470 | 152
AVG. | 7.8774 | 17.9474 | 0.1 | 1083.3684 | 632.3158 | 339.6842 | 292.6316 | 156.9474 | 3.7211 | 120.3158 | 0.1 | 353.5333 | 90.8947
No. of < Spec | 0 | -- | 19 | -- | -- | -- | -- | -- | 15 | -- | -- | -- | --
No. of > Spec | 0 | 6 | 0 | 0 | 0 | 0 | -- | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 0 | -- | 100 | -- | -- | -- | -- | -- | 78.9474 | - | - | - | --
% > Specs. | 0 | 31.5789 | 0 | 0 | 0 |  | -- | 0 | 0 | 0 | 0 | 0 | 0
No. of < Spec | 1 | -- | 3 | -- | -- | -- | -- | -- | 2 | -- | -- | -- | --
No. of > Spec | 1 | 1 | 1 | 0 | 0 | 0 | -- | 0 | 1 | 0 | 0 | 3 | 0
% < Specs. | 25 | -- | 75 | -- | -- | -- | -- | -- | 50 | - | - | - | --
% > Specs. | 25 | 33.3333 | 25 | 0 | 0 | 0 | -- | 0 | 25 | 0 | 0 | 100 | 0