## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.2-8.2 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2017-12-01 | 7.61 | 42 | 0.3 | 2065 | 1213 | 665 | 548 | 360 | 4 | 109 | 0.3 | 1075 | 230
2017-12-02 | 7.9 | 55 | 0.5 | 2098 | 1186 | 636 | 550 | 364 | 4 | 112 | 0.3 | 1030 | 228
2017-12-03 | 7.85 | 53 | 0.3 | 2130 | 1198 | 650 | 548 | 366 | 4 | 110 | 0.3 | 1028 | 228
2017-12-04 | 7.7 | 47 | 0.3 | 1982 | 1170 | 630 | 540 | 365 | 4 | 102 | 0.3 | 1020 | 220
2017-12-05 | 7.68 | 50 | 0.3 | 2018 | 1173 | 618 | 555 | 404 | 4 | 113 | 0.3 | 1030 | 230
2017-12-06 | 7.8 | 50 | 0.2 | 2200 | 1338 | 690 | 648 | 331 | 4 | 110 | 0.2 | 1025 | 234
2017-12-07 | 7.98 | 48 | 0.3 | 2290 | 1367 | 710 | 657 | 346 | 4.1 | 109 | 0.2 | 1034 | 240
2017-12-08 | 7.7 | 49 | 0.1 | 2230 | 1326 | 690 | 636 | 335 | 4 | 108 | 0.3 | 1024 | 238
2017-12-09 | 7.62 | 49 | 0.1 | 2210 | 1302 | 682 | 620 | 330 | 4 | 108 | 0.3 | 1022 | 226
2017-12-10 | 7.89 | 52 | 0.1 | 2242 | 1340 | 698 | 642 | 335 | 4 | 106 | 0.3 | 1082 | 230
2017-12-11 | 7.92 | 54 | 0.2 | 2260 | 1363 | 710 | 653 | 332 | 4 | 102 | 0.3 | 1120 | 232
2017-12-12 | 7.7 | 55 | 0.3 | 2240 | 1410 | 720 | 690 | 340 | 4.1 | 110 | 0.3 | 1140 | 242
2017-12-13 | 7.56 | 56 | 0.1 | 2293 | 1520 | 770 | 750 | 335 | 4.2 | 110 | 0.3 | 1130 | 243
2017-12-14 | 7.68 | 56 | 0.1 | 2118 | 1623 | 769 | 854 | 321 | 4 | 107 | 0.3 | 1128 | 247
2017-12-15 | 7.65 | 54 | 0.1 | 2010 | 1408 | 751 | 657 | 300 | 4 | 109 | 0.3 | 1118 | 239
2017-12-16 | 7.4 | 40 | 0.1 | 2096 | 1409 | 752 | 657 | 300 | 4 | 103 | 0.3 | 1087 | 230
2017-12-17 | 7.32 | 42 | 0.3 | 2110 | 1428 | 763 | 665 | 307 | 4 | 104 | 0.3 | 1080 | 232
2017-12-18 | 7.62 | 50 | 0.2 | 2269 | 1490 | 780 | 710 | 331 | 4 | 105 | 0.3 | 1092 | 237
2017-12-19 | 7.38 | 52 | 0.6 | 2230 | 1418 | 738 | 680 | 335 | 4.1 | 103 | 0.4 | 1123 | 240
2017-12-20 | 7.57 | 53 | 0.2 | 2282 | 1400 | 721 | 679 | 350 | 4 | 102 | 0.4 | 1102 | 230
2017-12-21 | 7.39 | 54 | 0.2 | 2290 | 1412 | 730 | 682 | 357 | 4 | 102 | 0.4 | 1110 | 233
2017-12-22 | 7.57 | 57 | 0.1 | 2276 | 1452 | 744 | 708 | 378 | 4 | 105 | 0.4 | 1142 | 244
2017-12-23 | 7.4 | 60 | 0.2 | 2450 | 1445 | 759 | 686 | 382 | 4 | 105 | 0.4 | 1153 | 250
2017-12-24 | 7.33 | 56 | 0.1 | 2410 | 1587 | 853 | 734 | 385 | 4 | 102 | 0.4 | 1126 | 239
2017-12-25 | 7.26 | 58 | 0.1 | 2430 | 1598 | 862 | 736 | 385 | 4.1 | 102 | 0.4 | 1130 | 240
2017-12-26 | 7.6 | 56 | 0.1 | 2480 | 1630 | 868 | 762 | 378 | 4 | 107 | 0.4 | 1130 | 248
2017-12-27 | 7.32 | 50 | 0.1 | 2610 | 1650 | 870 | 780 | 395 | 4 | 104 | 0.3 | 1133 | 265
2017-12-28 | 7.42 | 57 | 0.1 | 2690 | 1672 | 853 | 819 | 371 | 4 | 110 | 0.3 | 1092 | 250
2017-12-29 | 7.5 | 50 | 0.1 | 2583 | 1638 | 858 | 780 | 392 | 4.1 | 110 | 0.3 | 1080 | 237
2017-12-30 | 7.69 | 69 | 0.2 | 2670 | 1660 | 880 | 780 | 350 | 4 | 112 | 0.3 | 1098 | 248
2017-12-31 | 7.73 | 67 | 0.2 | 2693 | 1679 | 893 | 786 | 352 | 4.1 | 110 | 0.3 | 1088 | 252
MIN. | 7.26 | 40 | 0.1 | 1982 | 1170 | 618 | 540 | 300 | 4 | 102 | 0.2 | 1020 | 220
MAX. | 7.98 | 69 | 0.6 | 2693 | 1679 | 893 | 854 | 404 | 4.2 | 113 | 0.4 | 1153 | 265
AVG. | 7.6045 | 52.9355 | 0.2 | 2288.871 | 1435.6452 | 752.0323 | 683.6129 | 352 | 4.0258 | 106.8065 | 0.31935 | 1089.4194 | 238.129
No. of < Spec | 0 | -- | 14 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 31 | 1 | 25 | 31 | 22 | -- | 0 | 0 | 0 | 0 | 31 | 31
% < Specs. | 0 | -- | 45.1613 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 100 | 3.2258 | 80.6452 | 100 |  | -- | 0 | 0 | 0 | 0 | 100 | 100
No. of < Spec | 11 | -- | 15 | -- | -- | -- | -- | -- | 1 | -- | -- | -- | --
No. of > Spec | 0 | 31 | 3 | 26 | 31 | 24 | -- | 0 | 0 | 0 | 0 | 31 | 31
% < Specs. | 34.375 | -- | 46.875 | -- | -- | -- | -- | -- | 3.125 | - | - | - | --
% > Specs. | 0 | 100 | 9.375 | 83.871 | 100 | 0 | -- | 0 | 0 | 0 | 0 | 100 | 100