## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-03-01 | 7.94 | 32 | 1 | 1040 | 312 | 200 | 112 | 271 | 6.6 | 10.6 | 100 | 350 | 60
2017-03-02 | 8.2 | 27 | 0.1 | 1020 | 312 | 184 | 128 | 197 | 6.5 | 10.5 | 100 | 358 | 58
2017-03-03 | 7.8 | 29 | 0.1 | 1085 | 316 | 188 | 128 | 219 | 6.3 | 10.3 | 100 | 324 | 68
2017-03-04 | 7.61 | 31 | NIL | 1004 | 332 | 192 | 140 | 227 | 6.5 | 10.5 | 100 | 350 | 53
2017-03-05 | 7.8 | 30 | 0.1 | 1080 | 316 | 188 | 128 | 219 | 6.3 | 10.3 | 100 | 324 | 68
2017-03-06 | 7.48 | 42 | NIL | 995 | 280 | 144 | 136 | 256 | 6.4 | 10.4 | 100 | 340 | 55
2017-03-07 | 7.52 | 40 | 0.1 | 890 | 276 | 140 | 136 | 249 | 6.3 | 10.3 | 100 | 324 | 54
2017-03-08 | 8.02 | 34 | 0.2 | 890 | 284 | 144 | 140 | 243 | 6.2 | 10.2 | 100 | 362 | 54
2017-03-09 | 7.5 | 48 | 0.3 | 860 | 248 | 140 | 108 | 107 | 6.4 | 10.4 | 100 | 330 | 56
2017-03-10 | 7.9 | 44 | 0.1 | 820 | 256 | 144 | 112 | 205 | 6.7 | 10.7 | 103 | 335 | 52
2017-03-11 | 8 | 30 | NIL | 810 | 252 | 140 | 112 | 212 | 6.6 | 10.6 | 100 | 350 | 50
2017-03-12 | 7.65 | 23 | NIL | 960 | 248 | 148 | 100 | 280 | 6.3 | 10.3 | 100 | 350 | 66
2017-03-13 | 7.93 | 24 | NIL | 950 | 256 | 160 | 96 | 278 | 6.8 | 10.8 | 100 | 360 | 70
2017-03-14 | 7.93 | 34 | 1 | 998 | 260 | 152 | 108 | 219 | 6.4 | 10.4 | 100 | 340 | 50
2017-03-15 | 7.9 | 29 | 0.1 | 980 | 245 | 144 | 101 | 210 | 6.6 | 10.6 | 100 | 345 | 54
2017-03-16 | 7.64 | 29 | 0.5 | 840 | 244 | 120 | 124 | 154 | 6.3 | 10.3 | 102 | 350 | 50
2017-03-17 | 8 | 22 | NIL | 796 | 260 | 128 | 132 | 161 | 6.2 | 10.2 | 109 | 340 | 53
2017-03-18 | 7.9 | 21 | 0.1 | 784 | 256 | 124 | 132 | 168 | 6.5 | 10.5 | 106 | 345 | 57
2017-03-19 | 7.95 | 23 | 0.1 | 792 | 259 | 130 | 129 | 172 | 6.5 | 10.6 | 102 | 350 | 63
2017-03-20 | 7.89 | 18 | NIL | 794 | 252 | 122 | 130 | 163 | 6.3 | 10.3 | 100 | 340 | 50
2017-03-21 | 7.8 | 19 | NIL | 890 | 262 | 124 | 138 | 170 | 6.4 | 10.4 | 102 | 345 | 52
2017-03-22 | 7.84 | 34 | NIL | 970 | 268 | 144 | 124 | 212 | 6.1 | 10.1 | 100 | 328 | 52
2017-03-23 | 7.8 | 15 | 0.2 | 979 | 269 | 125 | 144 | 271 | 6.5 | 10.5 | 104 | 340 | 56
2017-03-24 | 7.65 | 22 | NIL | 967 | 268 | 144 | 124 | 180 | 6.5 | 10.5 | 102 | 350 | 58
2017-03-25 | 7.7 | 23 | 0.1 | 972 | 266 | 140 | 126 | 230 | 6.5 | 10.5 | 103 | 350 | 57
2017-03-26 | 7.84 | 25 | NIL | 970 | 268 | 144 | 124 | 212 | 6.1 | 10.1 | 100 | 354 | 52
2017-03-27 | 7.9 | 27 | NIL | 880 | 260 | 148 | 112 | 212 | 6.2 | 10.2 | 103 | 340 | 56
2017-03-28 | 7.5 | 22 | NIL | 892 | 264 | 144 | 120 | 212 | 6.6 | 10.6 | 100 | 350 | 59
2017-03-29 | 7.8 | 23 | NIL | 856 | 267 | 146 | 121 | 218 | 6.5 | 10.5 | 104 | 345 | 56
2017-03-30 | 8 | 18 | 0.1 | 840 | 260 | 140 | 120 | 219 | 6.3 | 10.3 | 102 | 340 | 60
2017-03-31 | 7.69 | 18 | NIL | 832 | 248 | 128 | 120 | 205 | 6.3 | 10.3 | 100 | 345 | 52
MIN. | 7.48 | 18 | 0.1 | 784 | 244 | 120 | 96 | 205 | 6.1 | 10.1 | 100 | 324 | 50
MAX. | 8.2 | 48 | 1 | 1085 | 332 | 200 | 144 | 280 | 6.8 | 10.8 | 109 | 362 | 70
AVG. | 7.809 | 27.6129 | 0.2625 | 917.2903 | 269.8065 | 147.0645 | 122.7419 | 211.3226 | 6.4097 | 10.4129 | 101.3548 | 343.6774 | 56.4839
No. of < Spec | 1 | -- | 10 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 2 | 26 | 2 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 3.2258 | -- | 62.5 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 6.4516 | 83.871 | 12.5 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0