## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5-8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-12-01 | 7.62 | 18 | 0.6 | 1290 | 674 | 369 | 305 | 303 | 6.7 | 10.7 | 110 | 887 | 140
2017-12-02 | 8.1 | 18 | 0.1 | 1449 | 692 | 387 | 305 | 310 | 6.8 | 10.8 | 115 | 790 | 142
2017-12-03 | 8.02 | 18 | 0.1 | 1430 | 674 | 370 | 304 | 312 | 7 | 11 | 114 | 792 | 144
2017-12-04 | 7.99 | 24 | 0.3 | 1410 | 640 | 350 | 290 | 310 | 6.9 | 10.9 | 113 | 752 | 137
2017-12-05 | 7.92 | 23 | 0.5 | 1460 | 649 | 355 | 294 | 317 | 7.1 | 11.1 | 119 | 740 | 142
2017-12-06 | 8.01 | 30 | 1 | 1440 | 786 | 482 | 304 | 308 | 6.7 | 10.7 | 112 | 740 | 132
2017-12-07 | 8.12 | 29 | 0.3 | 1480 | 734 | 418 | 316 | 317 | 7.2 | 11.2 | 112 | 793 | 148
2017-12-08 | 8.28 | 33 | 0.1 | 1443 | 720 | 443 | 277 | 310 | 7 | 11 | 110 | 764 | 144
2017-12-09 | 8.12 | 28 | 0.2 | 1392 | 680 | 412 | 268 | 312 | 7 | 11 | 115 | 732 | 142
2017-12-10 | 7.8 | 26 | 0.3 | 1373 | 685 | 410 | 275 | 300 | 6.9 | 10.9 | 112 | 789 | 140
2017-12-11 | 7.92 | 24 | 0.3 | 1398 | 680 | 390 | 290 | 302 | 7 | 11 | 110 | 790 | 142
2017-12-12 | 7.87 | 24 | 0.1 | 1208 | 640 | 390 | 250 | 253 | 6.9 | 10.9 | 113 | 750 | 146
2017-12-13 | 7.82 | 25 | 0.1 | 1187 | 643 | 390 | 253 | 243 | 7.1 | 11.1 | 114 | 759 | 142
2017-12-14 | 8.09 | 22 | 0.1 | 1120 | 608 | 367 | 241 | 228 | 7 | 11 | 113 | 784 | 148
2017-12-15 | 8 | 23 | 0.4 | 1109 | 628 | 354 | 274 | 243 | 7 | 11 | 112 | 742 | 146
2017-12-16 | 8.1 | 24 | 0.1 | 1092 | 613 | 348 | 265 | 238 | 6.9 | 10.9 | 110 | 753 | 135
2017-12-17 | 8.08 | 23 | 0.1 | 1070 | 604 | 334 | 270 | 235 | 6.9 | 10.9 | 110 | 752 | 134
2017-12-18 | 7.9 | 24 | 0.2 | 1118 | 632 | 372 | 260 | 232 | 6.8 | 10.8 | 109 | 730 | 142
2017-12-19 | 7.75 | 22 | 0.3 | 1033 | 618 | 370 | 248 | 214 | 6.9 | 10.9 | 110 | 733 | 140
2017-12-20 | 8.1 | 26 | 0.2 | 1142 | 639 | 363 | 276 | 230 | 6.9 | 10.9 | 112 | 740 | 133
2017-12-21 | 8.12 | 25 | 0.2 | 1169 | 640 | 369 | 271 | 224 | 7 | 11 | 110 | 750 | 130
2017-12-22 | 8.08 | 24 | 0.1 | 1180 | 682 | 370 | 312 | 257 | 6.8 | 10.8 | 113 | 772 | 134
2017-12-23 | 8.12 | 26 | 0.2 | 1240 | 755 | 416 | 339 | 278 | 7 | 11 | 112 | 790 | 144
2017-12-24 | 8.1 | 27 | 0.2 | 1253 | 773 | 429 | 344 | 278 | 6.8 | 10.8 | 110 | 788 | 142
2017-12-25 | 8.03 | 21 | 0.3 | 1271 | 700 | 380 | 320 | 235 | 7.1 | 11.1 | 112 | 793 | 148
2017-12-26 | 8.1 | 22 | 0.5 | 1375 | 790 | 472 | 318 | 250 | 7 | 11 | 116 | 810 | 130
2017-12-27 | 7.9 | 23 | 0.2 | 1530 | 750 | 460 | 290 | 270 | 7.1 | 11.1 | 113 | 820 | 140
2017-12-28 | 7.92 | 21 | 0.2 | 1462 | 819 | 490 | 329 | 257 | 6.9 | 10.9 | 118 | 773 | 132
2017-12-29 | 7.83 | 17 | 0.1 | 1363 | 762 | 472 | 290 | 250 | 7 | 11 | 118 | 768 | 134
2017-12-30 | 8.02 | 19 | 0.1 | 1350 | 772 | 480 | 292 | 242 | 6.9 | 10.9 | 119 | 780 | 132
2017-12-31 | 8 | 17 | 0.1 | 1372 | 760 | 453 | 307 | 248 | 7 | 11 | 118 | 789 | 130
MIN | 7.62 | 17 | 0.1 | 1033 | 604 | 334 | 241 | 214 | 6.7 | 10.7 | 109 | 730 | 130
MAX. | 8.28 | 33 | 1 | 1530 | 819 | 490 | 344 | 317 | 7.2 | 11.2 | 119 | 887 | 148
AVG. | 7.9945 | 23.4194 | 0.24516 | 1297.0645 | 691.6774 | 402.0968 | 288.5172 | 267.9355 | 6.9452 | 10.9452 | 113.0323 | 772.4194 | 139.1935
No. of < Spec | 0 | -- | 12 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 25 | 2 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 38.7097 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 80.6452 | 6.4516 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0