## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5-8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-06-01 | 8 | 25 | 0.3 | 1408 | 968 | 612 | 356 | 234 | 6.3 | 10.3 | 112 | 875 | 246
2017-06-02 | 8.02 | 30 | 0.5 | 1430 | 984 | 588 | 396 | 241 | 6.7 | 10.7 | 110 | 870 | 239
2017-06-03 | 8.01 | 19 | 0.1 | 1518 | 992 | 596 | 396 | 249 | 6.4 | 10.4 | 112 | 867 | 242
2017-06-04 | 8.05 | 17 | 0.1 | 1562 | 984 | 587 | 397 | 249 | 6.3 | 10.3 | 110 | 868 | 244
2017-06-05 | 8.02 | 19 | 0.1 | 1310 | 980 | 572 | 408 | 240 | 6.7 | 10.7 | 110 | 842 | 240
2017-06-06 | 7.9 | 16 | 0.1 | 1293 | 986 | 579 | 407 | 241 | 6.6 | 10.6 | 109 | 860 | 235
2017-06-07 | 7.72 | 23 | 0.1 | 1387 | 886 | 534 | 352 | 227 | 6.8 | 10.8 | 107 | 868 | 224
2017-06-08 | 7.73 | 18 | 0.1 | 1380 | 918 | 557 | 361 | 234 | 6.9 | 10.9 | 110 | 860 | 219
2017-06-09 | 7.89 | 22 | 0.1 | 1410 | 851 | 526 | 325 | 227 | 7 | 11 | 107 | 852 | 244
2017-06-10 | 7.94 | 20 | 0.1 | 1360 | 852 | 528 | 324 | 219 | 6.8 | 10.8 | 108 | 875 | 240
2017-06-11 | 7.9 | 24 | 0.1 | 1398 | 894 | 558 | 336 | 258 | 6.7 | 10.7 | 110 | 874 | 242
2017-06-12 | 7.86 | 22 | 0.1 | 1380 | 884 | 540 | 344 | 256 | 6.7 | 10.7 | 105 | 874 | 241
2017-06-13 | 7.95 | 24 | 0.1 | 1408 | 916 | 548 | 368 | 246 | 6.9 | 10.9 | 109 | 884 | 246
2017-06-14 | 8.18 | 27 | 0.1 | 1462 | 928 | 556 | 372 | 234 | 7.2 | 11.2 | 107 | 890 | 242
2017-06-15 | 7.92 | 22 | 0.1 | 1480 | 942 | 551 | 391 | 233 | 6.5 | 10.5 | 108 | 820 | 220
2017-06-16 | 8.24 | 24 | 0.5 | 1565 | 916 | 548 | 368 | 197 | 6.8 | 10.8 | 110 | 830 | 235
2017-06-17 | 8 | 28 | 0.2 | 1520 | 920 | 530 | 390 | 200 | 6.9 | 10.9 | 102 | 875 | 230
2017-06-18 | 8.12 | 30 | 0.2 | 1542 | 932 | 542 | 390 | 202 | 6.9 | 10.9 | 102 | 876 | 232
2017-06-19 | 8.1 | 27 | 0.1 | 1760 | 1002 | 662 | 340 | 234 | 6.7 | 10.7 | 110 | 882 | 230
2017-06-20 | 8.29 | 30 | 0.2 | 1560 | 959 | 658 | 301 | 241 | 6.9 | 10.9 | 112 | 892 | 219
2017-06-21 | 7.86 | 28 | 0.2 | 1450 | 924 | 629 | 295 | 227 | 6.8 | 10.8 | 109 | 880 | 210
2017-06-22 | 7.98 | 30 | 0.1 | 1512 | 918 | 620 | 298 | 234 | 6.5 | 10.5 | 105 | 879 | 214
2017-06-23 | 7.82 | 32 | 0.1 | 1575 | 969 | 648 | 321 | 241 | 7.2 | 11.2 | 109 | 790 | 210
2017-06-24 | 8 | 33 | 0.3 | 1433 | 940 | 600 | 340 | 234 | 7 | 11 | 106 | 785 | 202
2017-06-25 | 7.96 | 35 | 0.3 | 1458 | 952 | 618 | 334 | 232 | 7 | 11 | 106 | 786 | 204
2017-06-26 | 7.92 | 40 | 0.1 | 1540 | 932 | 593 | 339 | 241 | 6.9 | 10.9 | 104 | 772 | 200
2017-06-27 | 7.98 | 30 | 0.1 | 1398 | 925 | 638 | 287 | 234 | 6.8 | 10.8 | 109 | 765 | 205
2017-06-28 | 7.69 | 35 | 0.1 | 1435 | 924 | 628 | 296 | 249 | 6.9 | 10.9 | 110 | 749 | 198
2017-06-29 | 7.9 | 28 | 0.1 | 1490 | 878 | 590 | 288 | 234 | 6.7 | 10.7 | 105 | 720 | 195
2017-06-30 | 7.59 | 32 | 0.2 | 1422 | 852 | 565 | 287 | 249 | 7 | 11 | 110 | 740 | 182
MIN | 7.59 | 16 | 0.1 | 1293 | 851 | 526 | 287 | 197 | 6.3 | 10.3 | 102 | 720 | 182
MAX. | 8.29 | 40 | 0.5 | 1760 | 1002 | 662 | 408 | 258 | 7.2 | 11.2 | 112 | 892 | 246
AVG. | 7.9513 | 26.3333 | 0.16333 | 1461.5333 | 930.2667 | 583.3667 | 346.9 | 234.5667 | 6.7833 | 10.7833 | 108.1 | 840 | 224.3333
No. of < Spec | 0 | -- | 20 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 24 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 30
% < Specs. | 0 | -- | 66.6667 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 80 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 100