## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5-8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-03-01 | 8.2 | 20 | 0.1 | 1840 | 1146 | 620 | 526 | 339 | 6.9 | 10.9 | 118 | 768 | 155
2018-03-02 | 8.18 | 18 | 0.1 | 1820 | 1120 | 612 | 508 | 339 | 6.9 | 10.9 | 120 | 770 | 156
2018-03-03 | 8.23 | 17 | 0.3 | 1730 | 1016 | 563 | 453 | 346 | 6.8 | 10.8 | 116 | 783 | 160
2018-03-04 | 8.2 | 16 | 0.3 | 1710 | 1004 | 560 | 444 | 348 | 6.9 | 10.9 | 115 | 780 | 158
2018-03-05 | 8.2 | 22 | 0.1 | 1709 | 1063 | 566 | 497 | 320 | 6.7 | 10.7 | 118 | 764 | 154
2018-03-06 | 8.1 | 21 | 0.1 | 1702 | 1059 | 564 | 495 | 319 | 6.9 | 10.9 | 110 | 780 | 150
2018-03-07 | 8 | 18 | 0.1 | 1740 | 1032 | 534 | 498 | 310 | 6.8 | 10.8 | 115 | 790 | 150
2018-03-08 | 8.1 | 18 | 0.1 | 1670 | 1016 | 530 | 486 | 303 | 6.8 | 10.8 | 117 | 763 | 148
2018-03-09 | 8.002 | 15 | 0.1 | 1460 | 978 | 520 | 458 | 288 | 6.7 | 10.7 | 110 | 760 | 139
2018-03-10 | 8.22 | 16 | 0.1 | 1460 | 1004 | 557 | 447 | 298 | 6.8 | 10.8 | 118 | 782 | 148
2018-03-11 | 8.2 | 15 | 0.1 | 1438 | 990 | 540 | 450 | 294 | 6.8 | 10.8 | 116 | 790 | 150
2018-03-12 | 8.1 | 18 | 0.1 | 1538 | 865 | 469 | 396 | 288 | 6.9 | 10.9 | 114 | 789 | 144
2018-03-13 | 8.07 | 24 | 0.2 | 1540 | 873 | 481 | 392 | 295 | 6.9 | 10.9 | 115 | 763 | 148
2018-03-14 | 7.72 | 23 | 0.2 | 1435 | 877 | 436 | 441 | 303 | 6.9 | 10.9 | 112 | 782 | 159
2018-03-15 | 7.59 | 24 | 0.1 | 1690 | 1077 | 571 | 506 | 288 | 7 | 11 | 109 | 784 | 150
2018-03-16 | 7.89 | 17 | 0.1 | 1400 | 824 | 461 | 363 | 281 | 6.9 | 10.9 | 115 | 793 | 150
2018-03-17 | 7.9 | 17 | 0.1 | 1330 | 787 | 445 | 342 | 273 | 6.8 | 10.8 | 112 | 796 | 153
2018-03-18 | 7.82 | 18 | 0.1 | 1322 | 780 | 440 | 340 | 274 | 6.9 | 10.9 | 110 | 794 | 152
2018-03-19 | 7.9 | 19 | 0.1 | 1283 | 740 | 410 | 330 | 270 | 6.9 | 10.9 | 112 | 783 | 153
2018-03-20 | 7.81 | 15 | 0.1 | 1215 | 677 | 384 | 293 | 216 | 6.7 | 10.7 | 110 | 779 | 156
2018-03-21 | 8 | 18 | 0.1 | 1190 | 673 | 367 | 306 | 203 | 6.8 | 10.8 | 115 | 770 | 145
2018-03-22 | 8.06 | 16 | 0.1 | 1260 | 676 | 376 | 300 | 238 | 6.8 | 10.8 | 120 | 782 | 146
2018-03-23 | 8 | 16 | 0.1 | 1269 | 680 | 392 | 288 | 245 | 6.5 | 10.5 | 122 | 778 | 140
2018-03-24 | 7.9 | 14 | 0.1 | 1370 | 696 | 400 | 296 | 252 | 6.8 | 10.8 | 119 | 764 | 144
2018-03-25 | 7.92 | 13 | 0.1 | 1340 | 680 | 390 | 290 | 248 | 6.7 | 10.7 | 120 | 762 | 142
2018-03-26 | 8.02 | 16 | 0.1 | 1390 | 710 | 410 | 300 | 256 | 6.9 | 10.9 | 120 | 760 | 148
2018-03-27 | 7.68 | 17 | 0.1 | 1469 | 743 | 440 | 303 | 280 | 6.9 | 10.9 | 107 | 730 | 144
2018-03-28 | 7.81 | 16 | 0.1 | 1460 | 816 | 420 | 396 | 268 | 6.9 | 10.9 | 110 | 763 | 142
2018-03-29 | 7.83 | 17 | 0.2 | 1480 | 840 | 433 | 407 | 287 | 6.7 | 10.7 | 115 | 783 | 149
2018-03-30 | 8.02 | 18 | 0.2 | 1570 | 880 | 453 | 427 | 289 | 6.5 | 10.5 | 114 | 720 | 150
2018-03-31 | 7.98 | 19 | 0.1 | 1520 | 890 | 502 | 388 | 320 | 6.9 | 10.9 | 118 | 733 | 150
MIN | 7.59 | 13 | 0.1 | 1190 | 673 | 367 | 288 | 203 | 6.5 | 10.5 | 107 | 720 | 139
MAX. | 8.23 | 24 | 0.3 | 1840 | 1146 | 620 | 506 | 348 | 7 | 11 | 122 | 796 | 160
AVG. | 7.9888 | 17.7742 | 0.12581 | 1495.1613 | 877.8065 | 478.9032 | 390.7586 | 286.3871 | 6.8161 | 10.8161 | 114.9032 | 772.1935 | 149.4516
No. of < Spec | 0 | -- | 25 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 5 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 80.6452 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 16.129 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0