## Word file
Wex Tech
2013-04-05
COOLING WATER TREATMENT
DCM SRIRAM LIMITED
MONTHLY REPORT
REPORT
OF
COOLING TOWER
DATE : |  | 2013-05-07
Sriram Chemical Ltd.,
Jagadia, Ankleshwar
Gujarat
Kind Attn : Sh. K. R. Vaidya (Unit Head)
Subject : Cooling Water Treatment Monthly Report
Dear Sir,
Please find enclosed herewith the CWT Monthly Report for your
Cooling water system for the Month of | [5 empty] | 2013-04-05
The report is based on the laboratory analysis done by our |  |  |  |  | 41369
representative in presence of your laboratory in charge and data
collected from the Control Room.
If you need any clarification, please feel free to contact us.
Assuring you of our best services at all times.
Thanking you,
Yours sincerely,
FOR WEX TECHNOLOGIES PVT. LTD.
Vipul Govekar
Regional Manager
Encl. : a/a | : a/a
C.C. : MR. R. R. BULDAK
MR. NAVIN JAISWAL
MR. U. D. MEHTA
MR. SUNIT GUPTA
MR. ATUL CHOKSI
EXECUTIVE SUMMARY
1] | EXCEPTIONS CIRCULATING WATER PARAMETERS
• | pH was very well maintained within the specified limits throughout the month.
• | Turbidity was also very well maintained within its specified limits throughout the month.
• | FRC was reported on lower side on three occasions due to unavailability of chlorine toner. We request to ensure availability of spare toner at site all the time.
• | Conductivity was well maintained within the specified limits.
• | Total Hardness well maintained within its specified limits.
• | CaH was also very well maintained within its specified limits.
• | Chloride was well maintained within its specified limits.
• | Ortho Phosphate was also very well maintained within the specified limits.
• | Plant was running smoothly and no any major abnormality was reported except low FRC for three days.
2] | COOLING WATER PARAMETERS
| Sr. No. |  | Parameters |  | Control Limits | Min. | Max. | Avg.
| 1 |  | pH |  | 7.5-8.0 | 7.59 | 8.12 | 7.939
| 2 |  | Turbidity |  | Max. 20 NTU | 18 | 121 | 45.8333
| 3 |  | FRC |  | 0.2 - 0.5 ppm | 0.1 | 0.2 | 0.19667
| 4 |  | TDS |  | Max. 2100 ppm | 1218 | 1995 | 1560.4
| 5 |  | TH |  | Max. 1200 ppm | 672 | 1102 | 904.4333
| 6 |  | Cl |  | Max. 500 ppm | 103 | 196 | 152.0333
| 7 |  | Ortho PO4 |  | 4.0 - 6.0 ppm | 5.7 | 8 | 6.94
| 8 |  | T. Alk. |  | Max. 200 ppm | 120 | 185 | 166.7333
| 9 |  | Total Iron |  | Max. 2 ppm | 0.2 | 0.3 | 0.20667
| 10 |  | Sulphate |  | Max. 1000 ppm | 893 | 984 | 932.8
| 11 |  | Silica |  | 180 ppm | 91 | 121 | 109.0333
3] | MAKE UP WATER PARAMETERS
| Sr. No. |  | Parameters |  | Unit | Min. | Max. | Avg.
| 1 |  | pH |  | -- | 7.8 | 8.12 | 8.0117
| 2 |  | Turb. |  | NTU | 2 | 3 | 2.3667
| 3 |  | Cond |  | mS | 250 | 365 | 283.7667
| 4 |  | TDS |  | ppm | 170 | 220 | 190.3333
| 5 |  | TH |  | ppm | 112 | 128 | 120.4667
| 6 |  | Cl |  | ppm | 36 | 36 | 33
| 7 |  | Silica |  | ppm | 17 | 21 | 18.9667
| 8 |  | T. Alk. |  | ppm | 155 | 172 | 164.8333
3] | Monthly Compliance Analysis
| Sr. No. |  | Parameters |  | Control Limits | < Limits | > Limits | % Compliance
| 1 |  | pH |  | 7.5-8.0 | 0 | 6 | 80
| 2 |  | Turbidity |  | Max. 20 NTU | -- | 28 | 3.4483
| 3 |  | FRC |  | 0.2 - 0.5 ppm | 1 | 0 | 96.4286
| 4 |  | TDS |  | Max. 2100 ppm | -- | 0 | 100
| 5 |  | TH |  | Max. 1200 ppm | -- | 0 | 100
| 6 |  | Cl |  | Max. 500 ppm | -- | 0 | 100
| 7 |  | Ortho PO4 |  | 4.0 - 6.0 ppm | 0 | 27 | -12.5
| 8 |  | T. Alk. |  | Max. 200 ppm | -- | 0 | 100
| 9 |  | Total Iron |  | Max. 2 ppm | -- | 0 | 100
| 10 |  | Sulphate |  | Max. 1000 ppm | -- | 0 | 100
| 11 |  | Silica |  | 180 ppm | -- | 0 | 100

## MakeUp
MAKE UP WATER ANALYSIS
Date | pH | Turb. | Cond | TDS | TH | CaH | Cl | Silica | T. Alk. | P. Alk.
Unit | -- | NTU | us/cm | ppm | ppm | ppm | ppm | ppm | ppm | ppm
2013-04-01 | 8.03 | 3 | 325 | 220 | 128 | 71 | 28 | 20 | 165 | NIL
2013-04-02 | 8.08 | 3 | 365 | 180 | 122 | 70 | 25 | 20 | 170 | NIL
2013-04-03 | 8.05 | 2 | 258 | 175 | 120 | 70 | 25 | 18 | 165 | NIL
2013-04-04 | 8.01 | 2 | 273 | 185 | 125 | 71 | 26 | 18 | 165 | NIL
2013-04-05 | 8.07 | 2 | 266 | 180 | 122 | 70 | 26 | 19 | 170 | NIL
2013-04-06 | 8.12 | 2 | 280 | 190 | 123 | 70 | 25 | 19 | 172 | NIL
2013-04-07 | 8.1 | 3 | 295 | 200 | 125 | 71 | 26 | 19 | 170 | NIL
2013-04-08 | 8.1 | 3 | 310 | 210 | 127 | 72 | 27 | 20 | 170 | NIL
2013-04-09 | 8.06 | 3 | 295 | 200 | 125 | 71 | 26 | 20 | 168 | NIL
2013-04-10 | 8.02 | 3 | 303 | 205 | 122 | 70 | 27 | 20 | 165 | NIL
2013-04-11 | 7.98 | 2 | 295 | 200 | 121 | 70 | 26 | 19 | 162 | NIL
2013-04-12 | 8.05 | 2 | 273 | 185 | 122 | 70 | 25 | 19 | 165 | NIL
2013-04-13 | 8.07 | 3 | 295 | 200 | 125 | 71 | 26 | 20 | 165 | NIL
2013-04-14 | 8.05 | 3 | 288 | 195 | 125 | 71 | 25 | 20 | 162 | NIL
2013-04-15 | 8.02 | 3 | 280 | 190 | 124 | 70 | 25 | 19 | 162 | NIL
2013-04-16 | 8.08 | 2 | 295 | 200 | 128 | 72 | 26 | 20 | 170 | NIL
2013-04-17 | 7.9 | 2 | 273 | 185 | 125 | 71 | 25 | 18 | 160 | NIL
2013-04-18 | 7.95 | 2 | 266 | 180 | 120 | 69 | 28 | 19 | 162 | NIL
2013-04-19 | 7.9 | 2 | 273 | 185 | 118 | 69 | 27 | 20 | 160 | NIL
2013-04-20 | 7.8 | 2 | 280 | 190 | 115 | 68 | 26 | 20 | 155 | NIL
2013-04-21 | 7.95 | 3 | 295 | 200 | 115 | 68 | 25 | 21 | 165 | NIL
2013-04-22 | 7.9 | 3 | 310 | 210 | 117 | 68 | 25 | 19 | 160 | NIL
2013-04-23 | 8.02 | 2 | 288 | 195 | 120 | 69 | 21 | 19 | 165 | NIL
2013-04-24 | 8.06 | 2 | 280 | 190 | 117 | 68 | 21 | 18 | 168 | NIL
2013-04-25 | 8.08 | 2 | 258 | 175 | 114 | 67 | 18 | 17 | 170 | NIL
2013-04-26 | 8.05 | 2 | 251 | 170 | 113 | 67 | 18 | 17 | 165 | NIL
2013-04-27 | 7.98 | 2 | 266 | 180 | 114 | 67 | 18 | 17 | 162 | NIL
2013-04-28 | 7.95 | 2 | 250 | 178 | 113 | 66 | 16 | 18 | 162 | NIL
2013-04-29 | 7.9 | 2 | 258 | 175 | 112 | 66 | 16 | 18 | 160 | NIL
2013-04-30 | 8.02 | 2 | 269 | 182 | 117 | 68 | 16 | 18 | 165 | NIL
MIN. | 7.8 | 2 | 250 | 170 | 112 | 66 | 36 | 17 | 155 | NIL
MAX. | 8.12 | 3 | 365 | 220 | 128 | 72 | 36 | 21 | 172 | NIL
AVG. | 8.0117 | 2.3667 | 283.7667 | 190.3333 | 120.4667 | 69.3667 | 33 | 18.9667 | 164.8333 | #DIV/0!

## Cooling Tower
CIRCULATING WATER ANALYSIS FOR COOLING TOWER
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | Silica
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2013-04-01 | 7.59 | 121 | 0.2 | 2390 | 1618 | 1102 | 672 | 430 | 146 | 6.5 | 120 | NIL | 0.2 | 240 | 893 | 95
2013-04-02 | 7.86 | 118 | 0.2 | 2190 | 1479 | 918 | 560 | 358 | 125 | 7.2 | 150 | NIL | 0.2 | 236 | 984 | 91
2013-04-03 | 7.92 | 104 | 0.2 | 2100 | 1420 | 898 | 530 | 368 | 132 | 6.8 | 160 | NIL | 0.2 | 208 | 916 | 98
2013-04-04 | 7.98 | 85 | 0.2 | 2180 | 1470 | 877 | 510 | 367 | 125 | 8 | 165 | NIL | 0.2 | 170 | 966 | 110
2013-04-05 | 7.9 | 77 | 0.2 | 2150 | 1450 | 816 | 449 | 367 | 114 | 7.1 | 160 | NIL | 0.2 | 154 | 952 | 113
2013-04-06 | 7.8 | 62 | 0.2 | 2010 | 1360 | 775 | 428 | 347 | 110 | 7 | 150 | NIL | 0.2 | 120 | 938 | 108
2013-04-07 | 8.02 | 50 | 0.2 | 2000 | 1353 | 672 | 401 | 271 | 103 | 7 | 170 | NIL | 0.2 | 98 | 942 | 110
2013-04-08 | 8 | 49 | 0.2 | 1995 | 1348 | 726 | 416 | 310 | 114 | 7 | 170 | NIL | 0.2 | 90 | 956 | 112
2013-04-09 | 7.9 | 41 | 0.2 | 2050 | 1431 | 747 | 428 | 319 | 117 | 6.9 | 160 | NIL | 0.2 | 80 | 943 | 110
2013-04-10 | 7.88 | 52 | 0.1 | 2215 | 1550 | 726 | 420 | 306 | 114 | 6.8 | 160 | NIL | 0.2 | 101 | 929 | 108
2013-04-11 | 8.09 | 45 | 0.2 | 1740 | 1218 | 734 | 428 | 306 | 117 | 7 | 170 | NIL | 0.2 | 88 | 910 | 110
2013-04-12 | 7.98 | 37 | 0.2 | 1795 | 1256 | 747 | 428 | 319 | 125 | 6.8 | 170 | NIL | 0.2 | 74 | 925 | 108
2013-04-13 | 8.12 | 38 | 0.2 | 1968 | 1378 | 804 | 469 | 335 | 132 | 7.1 | 180 | NIL | 0.2 | 60 | 938 | 112
2013-04-14 | 7.94 | 22 | 0.2 | 2110 | 1477 | 849 | 510 | 339 | 189 | 7.1 | 165 | NIL | 0.2 | 48 | 949 | 110
2013-04-15 | 7.98 | 23 | 0.2 | 2128 | 1490 | 856 | 518 | 338 | 196 | 7.2 | 170 | NIL | 0.2 | 40 | 936 | 102
2013-04-16 | 8.02 | 38 | 0.2 | 1985 | 1390 | 918 | 694 | 224 | 160 | 7.2 | 180 | NIL | 0.3 | 75 | 921 | 108
2013-04-17 | 7.89 | 29 | 0.2 | 2084 | 1459 | 938 | 550 | 388 | 164 | 7.1 | 165 | NIL | 0.3 | 76 | 910 | 105
2013-04-18 | 7.8 | 24 | 0.2 | 2142 | 1500 | 971 | 571 | 400 | 171 | 7 | 160 | NIL | 0.2 | 45 | 924 | 108
2013-04-19 | 7.8 | 39 | 0.2 | 2150 | 1504 | 1089 | 679 | 410 | 175 | 5.8 | 160 | NIL | 0.2 | 76 | 930 | 110
2013-04-20 | 7.96 | 60 | 0.2 | 2140 | 1495 | 969 | 575 | 394 | 175 | 5.7 | 170 | NIL | 0.2 | 110 | 935 | 113
2013-04-21 | 8.05 | 23 | 0.2 | 2142 | 1500 | 990 | 580 | 410 | 178 | 5.9 | 180 | NIL | 0.2 | 50 | 960 | 115
2013-04-22 | 7.99 | 26 | 0.2 | 2850 | 1995 | 1040 | 582 | 458 | 189 | 7.2 | 185 | NIL | 0.2 | 45 | 946 | 121
2013-04-23 | 7.98 | 23 | 0.2 | 2690 | 1883 | 986 | 574 | 412 | 178 | 7.1 | 182 | NIL | 0.2 | 42 | 930 | 118
2013-04-24 | 7.97 | 19 | 0.2 | 2880 | 1960 | 1019 | 624 | 395 | 189 | 7 | 180 | NIL | 0.2 | 35 | 912 | 111
2013-04-25 | 8.02 | 18 | 0.2 | 2571 | 1800 | 953 | 562 | 391 | 164 | 7 | 185 | NIL | 0.2 | 30 | 898 | 102
2013-04-26 | 7.98 | 35 | 0.2 | 2592 | 1815 | 1019 | 603 | 416 | 174 | 7 | 170 | NIL | 0.2 | 62 | 915 | 108
2013-04-27 | 7.89 | 30 | 0.2 | 2595 | 1816 | 1027 | 611 | 416 | 178 | 7.1 | 165 | NIL | 0.2 | 60 | 930 | 110
2013-04-28 | 7.9 | 32 | 0.2 | 2600 | 1818 | 1028 | 613 | 415 | 176 | 7.3 | 160 | NIL | 0.2 | 62 | 935 | 115
2013-04-29 | 7.98 | 31 | 0.2 | 2685 | 1880 | 1040 | 624 | 416 | 178 | 7.1 | 170 | NIL | 0.2 | 63 | 943 | 120
2013-04-30 | 7.98 | 24 | 0.2 | 2427 | 1699 | 899 | 556 | 343 | 153 | 7.2 | 170 | NIL | 0.2 | 44 | 918 | 110
MIN. | 7.59 | 18 | 0.1 | 1740 | 1218 | 672 | 401 | 224 | 103 | 5.7 | 120 | 0 | 0.2 | 30 | 893 | 91
MAX. | 8.12 | 121 | 0.2 | 2880 | 1995 | 1102 | 694 | 458 | 196 | 8 | 185 | 0 | 0.3 | 240 | 984 | 121
AVG. | 7.939 | 45.8333 | 0.19667 | 2251.8 | 1560.4 | 904.4333 | 538.8333 | 365.6 | 152.0333 | 6.94 | 166.7333 | #DIV/0! | 0.20667 | 89.4 | 932.8 | 109.0333
No. of < Spec | 0 | -- | 1 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 6 | 28 | 0 | -- | 0 | 0 | -- | -- | 0 | 27 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 3.3333 | -- | -- | -- | -- | -- | -- | 0 | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | --
% > Specs. | 20 | 93.3333 | 0 | #VALUE! | 0 | 0 | #VALUE! | -- | 0 | 90 | 0 | #DIV/0! | 0 | #VALUE! | 0 | 0

## Operational Parameters
Power Plant Data & Operational Parameters
Date | Plant Load | Vacumm | COC Based on (TH) | COC Based on (Silica) | CT Blowdown
| MW | Kgs./Cm2 |  |  | M3/Hr.
2013-04-01 |  |  | 8.6094 | 4.75
2013-04-02 |  |  | 7.5246 | 4.55
2013-04-03 |  |  | 7.4833 | 5.4444
2013-04-04 |  |  | 7.016 | 6.1111
2013-04-05 |  |  | 6.6885 | 5.9474
2013-04-06 |  |  | 6.3008 | 5.6842
2013-04-07 |  |  | 5.376 | 5.7895
2013-04-08 |  |  | 5.7165 | 5.6
2013-04-09 |  |  | 5.976 | 5.5
2013-04-10 |  |  | 5.9508 | 5.4
2013-04-11 |  |  | 6.0661 | 5.7895
2013-04-12 |  |  | 6.123 | 5.6842
2013-04-13 |  |  | 6.432 | 5.6
2013-04-14 |  |  | 6.792 | 5.5
2013-04-15 |  |  | 6.9032 | 5.3684
2013-04-16 |  |  | 7.1719 | 5.4
2013-04-17 |  |  | 7.504 | 5.8333
2013-04-18 |  |  | 8.0917 | 5.6842
2013-04-19 |  |  | 9.2288 | 5.5
2013-04-20 |  |  | 8.4261 | 5.65
2013-04-21 |  |  | 8.6087 | 5.4762
2013-04-22 |  |  | 8.8889 | 6.3684
2013-04-23 |  |  | 8.2167 | 6.2105
2013-04-24 |  |  | 8.7094 | 6.1667
2013-04-25 |  |  | 8.3596 | 6
2013-04-26 |  |  | 9.0177 | 6.3529
2013-04-27 |  |  | 9.0088 | 6.4706
2013-04-28 |  |  | 9.0973 | 6.3889
2013-04-29 |  |  | 9.2857 | 6.6667
2013-04-30 |  |  | 7.6838 | 6.1111
0 |  |  | #DIV/0! | #DIV/0!
MIN. | 0 | 0 | #DIV/0! | #DIV/0! | 0
MAX. | 0 | 0 | #DIV/0! | #DIV/0! | 0
AVG. | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Chemical Consumption
Chemical Consumption for Cooling Tower
Sr. No. | Chemical Name | Specified Monthly Consumption (Kgs.) | Opening Stock (Kgs.) |  |  | Receipt in Store (Kgs.) | Actual Consumption (Kgs.) | Closing Balance (Kgs.)
|  |  | At Store | At Utility | Total Stock |  |  | At Store | At Utility | Total Stock
1
2
3
4
5
6